## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Firstlight Network Limited
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Firstlight Network Limited
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | 3564-26 | Mahia, Newcastle St, Fortescue St | Wairoa | Mahia 3301 | 2025-04-01 09:02 | 45748.3764 | 2025-04-01 15:07 | 45748.6299 | 5.1957 | 0.014256 | 373 | 67245.0425 | Planned | Planned | Replace Aerial stub poles
10 |  | 1770-26 | Paparatu Road | Gisborne | Te Arai 0906 | 2025-04-01 15:46 | 45748.6569 | 2025-04-01 16:32 | 45748.6889 | 0.0279 | 0.0006115 | 16 | 730 | Unplanned | Defective Equipment | Burnt HV Pole C863. Insulator failed tracked thru arm. - Also see 2024/25 Yr Rows1626-1627
11 |  | 3549-26 | Back Ormond Road | Gisborne | Waimata 0903 | 2025-04-02 09:03 | 45749.3771 | 2025-04-02 10:26 | 45749.4347 | 0.050755 | 0.0006115 | 16 | 664.406 | Planned | Planned | Replace TX C539
12 |  | 6000-26 | 209 Waiatai Valley Road | Wairoa | Nuhaka 3203 | 2025-04-02 10:53 | 45749.4535 | 2025-04-02 11:53 | 45749.4951 | 0.029811 | 0.00049685 | 13 | 780 | Unplanned | Unknown cause | Replace DDO fuses
13 |  | 6002-26 | Pitcher Road | Gisborne | Te Karaka 1203 | 2025-04-02 11:02 | 45749.4597 | 2025-04-02 12:02 | 45749.5014 | 0.016052 | 0.00026753 | 7 | 420 | Unplanned | Unknown cause | Replace DDO fuses
14 |  | 6001-26 | 1381 Hereheretau Road | Wairoa | Nuhaka 3203 | 2025-04-02 15:31 | 45749.6465 | 2025-04-02 16:31 | 45749.6882 | 0.04357 | 0.00072616 | 19 | 1140 | Unplanned | Unknown cause | Replace DDO fuses
15 |  | 3570-26 | Tuai Main Road | Wairoa | Village 2002 | 2025-04-03 09:03 | 45750.3771 | 2025-04-03 12:46 | 45750.5319 | 0.86933 | 0.0038983 | 102 | 22746 | Planned | Planned | Replace HV poles
16 |  | 6004-26 | 23 Mangaone Road | Gisborne | Kanakanaia 1202 | 2025-04-03 10:25 | 45750.434 | 2025-04-03 11:25 | 45750.4757 | 0.018345 | 0.00030575 | 8 | 480 | Unplanned | Unknown cause | Replace DDO fuses
17 |  | 6003-26 | 849 Pehiri Road | Gisborne | Tahunga 1004 | 2025-04-03 11:21 | 45750.4729 | 2025-04-03 12:51 | 45750.5354 | 0.024078 | 0.00026753 | 7 | 630 | Unplanned | Unknown cause | Replace DDO fuses
18 |  | 3559-26 | Waingake Road | Gisborne | Te Arai 0906 | 2025-04-03 13:00 | 45750.5417 | 2025-04-03 14:07 | 45750.5882 | 0.10461 | 0.0017581 | 46 | 1369.703 | Planned | Planned | Install D/A & DDOs on existing pole C754
19 |  | 6005-26 | Pitcher Road | Gisborne | Te Karaka 1203 | 2025-04-03 13:20 | 45750.5556 | 2025-04-03 15:50 | 45750.6597 | 0.04013 | 0.00026753 | 7 | 1050 | Unplanned | Unknown cause | Replace DDO fuses
20 |  | 1771-26 | Pitchers Road | Gisborne | Te Karaka 1203 | 2025-04-03 16:48 | 45750.7 | 2025-04-03 17:48 | 45750.7417 | 0.01437 | 0.00026753 | 7 | 376 | Unplanned | Wildlife | Bird came in contact with the HV conductor at Pole E1539
21 |  | 3572A-26 | Mangaoporo Road / Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-04-04 09:09 | 45751.3812 | 2025-04-04 12:42 | 45751.5292 | 0.13698 | 0.00064972 | 17 | 3584 | Planned | Planned | Tree clearing at poles J2274 & J2729
22 |  | 3572-26 | Mangaoporo Road / Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-04-04 09:12 | 45751.3833 | 2025-04-04 12:41 | 45751.5285 | 0.095853 | 0.00045863 | 12 | 1254.8255 | Planned | Planned | Tree clearing at poles J2274 & J2729
23 |  | 6006-26 | 1890 East Cape Road | Gisborne | Tiki Tiki 0206 | 2025-04-05 07:44 | 45752.3222 | 2025-04-05 09:14 | 45752.3847 | 0.048156 | 0.00053507 | 14 | 1260 | Unplanned | Unknown cause | Replace DDO fuses
24 |  | 6007-26 | 3960 SH 2 | Wairoa | Morere 3401 | 2025-04-06 14:58 | 45753.6236 | 2025-04-06 15:58 | 45753.6653 | 0.0022931 | 3.8219e-05 | 1 | 60 | Unplanned | Unknown cause | Replace DDO fuses
25 |  | 6008-26 | 171 Pauariki Road | Gisborne | Mata 0304 | 2025-04-07 06:21 | 45754.2646 | 2025-04-07 06:51 | 45754.2854 | 0.0045863 | 0.00015288 | 4 | 120 | Unplanned | Unknown cause | Replace DDO fuses
26 |  | 3588-26 | Arapata Road | Wairoa | Raupunga 3101 | 2025-04-07 09:03 | 45754.3771 | 2025-04-07 17:39 | 45754.7354 | 0.3218 | 0.0016434 | 43 | 3525.1017 | Planned | Planned | To dismantle 11kV line and install generator
27 |  | 6009-26 | 365 Lottin Point Road | Gisborne | Hicks Bay 0102 | 2025-04-07 15:39 | 45754.6521 | 2025-04-07 17:09 | 45754.7146 | 0.041277 | 0.00045863 | 12 | 1080 | Unplanned | Unknown cause | Replace DDO fuses
28 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Ruatoria LS 0220 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:48 | 45755.3667 | 0.00030575 | 3.8219e-05 | 1 | 8 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
29 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Ruatoria 0201 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:48 | 45755.3667 | 0.094477 | 0.01181 | 309 | 2472 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
30 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Makarika 0204 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:48 | 45755.3667 | 0.03455 | 0.0043187 | 113 | 904 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
31 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Tiki Tiki 0206 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:48 | 45755.3667 | 0.096006 | 0.012001 | 314 | 2512 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
32 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Te Araroa LS 0120 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:49 | 45755.3674 | 0.00034397 | 3.8219e-05 | 1 | 9 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
33 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Awatere 0101 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:49 | 45755.3674 | 0.031301 | 0.0034779 | 91 | 819 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
34 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Hicks Bay 0102 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:49 | 45755.3674 | 0.088745 | 0.0098605 | 258 | 2322 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
35 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Te Araroa 0103 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:49 | 45755.3674 | 0.043684 | 0.0048538 | 127 | 1143 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
36 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Mata 0304 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:52 | 45755.3694 | 0.1275 | 0.010625 | 278 | 3336 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
37 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Inland 0301 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:55 | 45755.3715 | 0.091726 | 0.006115 | 160 | 2400 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
38 |  | 1772-26 | Tokomaru Bay / Ruatoria / Te Araroa | Gisborne | Seaside 0302 | 2025-04-08 08:40 | 45755.3611 | 2025-04-08 08:57 | 45755.3729 | 0.077967 | 0.0045863 | 120 | 2040 | Unplanned | Unknown cause | Gis-Toko 50kV - Heli patrol Wed 9/4 No obvious fault. Weather 8/4 - High/Gusty wind. Cct restored w/out incident
39 |  | 3573-26 | Poroporo Road | Gisborne | Tiki Tiki 0206 | 2025-04-08 09:02 | 45755.3764 | 2025-04-08 15:29 | 45755.6451 | 0.17749 | 0.00045863 | 12 | 2323.0649 | Planned | Planned | Tree Cutting
40 |  | 3575-26 | Kakariki Farm Road | Wairoa | Raupunga 3101 | 2025-04-08 09:16 | 45755.3861 | 2025-04-08 13:47 | 45755.5743 | 0.082859 | 0.00030575 | 8 | 1084.3669 | Planned | Planned | Replace pole W5285
41 |  | 1774-26 | Whatatutu Road | Gisborne | Whatatutu 1201 | 2025-04-08 10:10 | 45755.4236 | 2025-04-08 17:05 | 45755.7118 | 3.9098 | 0.0094783 | 248 | 102300 | Unplanned | Vegetation | Tree across line @ F2792
42 |  | 1773-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-04-08 10:15 | 45755.4271 | 2025-04-08 11:37 | 45755.484 | 0.16923 | 0.0020638 | 54 | 4428 | Unplanned | Defective Equipment | Broken Jumper TX F259
43 |  | 1775-26 | Motu Road | Gisborne | Matawai 1204 | 2025-04-08 10:22 | 45755.4319 | 2025-04-08 17:07 | 45755.7132 | 0.83092 | 0.0023696 | 62 | 21741 | Unplanned | Vegetation | Tree through HV line @ F2611 - F2614
44 |  | 6010-26 | 195 Lane Road Mahia | Wairoa | Mahia 3301 | 2025-04-08 17:39 | 45755.7354 | 2025-04-08 18:39 | 45755.7771 | 0.0068794 | 0.00011466 | 3 | 180 | Unplanned | Unknown cause | Replace DDO fuses
45 |  | 6011-26 | 119 Kiekie Road | Gisborne | Inland 0301 | 2025-04-08 18:21 | 45755.7646 | 2025-04-08 18:51 | 45755.7854 | 0.0045863 | 0.00015288 | 4 | 120 | Unplanned | Unknown cause | Replace DDO fuses
46 |  | 6012-26 | 119 Kiekie Road | Gisborne | Inland 0301 | 2025-04-09 08:12 | 45756.3417 | 2025-04-09 09:12 | 45756.3833 | 0.0091726 | 0.00015288 | 4 | 240 | Unplanned | Unknown cause | Replace DDO fuses
47 |  | 3583-26 | Wheatstone Road | Gisborne | Dalton 0502 | 2025-04-09 09:01 | 45756.3757 | 2025-04-09 13:35 | 45756.566 | 0.30369 | 0.0011084 | 29 | 7946 | Planned | Planned | Replace Poles
48 |  | 6013-26 | 101 Pitcher Road | Gisborne | Te Karaka 1203 | 2025-04-09 12:41 | 45756.5285 | 2025-04-09 13:11 | 45756.5493 | 0.008026 | 0.00026753 | 7 | 210 | Unplanned | Unknown cause | Replace DDO fuses
49 |  | 1776-26 | East Coast Road | Wairoa | Mahia 3301 | 2025-04-09 23:01 | 45756.959 | 2025-04-10 11:37 | 45757.484 | 5.4123 | 0.0085611 | 224 | 141613 | Unplanned | Wildlife | Wires down @ TX W722 - HV through 400V. Potential bird strike due to tangled condition of conductor
50 |  | 3603-26 | Marumoko Road | Gisborne | Matawai 1204 | 2025-04-10 09:01 | 45757.3757 | 2025-04-10 14:36 | 45757.6083 | 0.61456 | 0.0018345 | 48 | 16080 | Planned | Planned | Urgent Work - Install new DDO @ F2609. Replace poles F2609 & F2610
51 |  | 3590-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-04-11 08:40 | 45758.3611 | 2025-04-11 15:38 | 45758.6514 | 0.25561 | 0.0006115 | 16 | 3346.0449 | Planned | Planned | Replace HV Poles
52 |  | 3602-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-04-11 09:07 | 45758.3799 | 2025-04-11 10:31 | 45758.4382 | 0.42094 | 0.0064972 | 170 | 11014 | Planned | Planned | Replace 11kV crossarm
53 |  | 3582-26 | Clifton, Lyall | Wairoa | Frasertown 3103 | 2025-04-11 09:09 | 45758.3812 | 2025-04-11 12:39 | 45758.5271 | 0.032104 | 0.00015288 | 4 | 840 | Planned | Planned | Replace Poles
54 |  | 6014-26 | 158 Ruataniwha Road | Wairoa | Brickworks 3201 | 2025-04-12 04:38 | 45759.1931 | 2025-04-12 05:08 | 45759.2139 | 0.04013 | 0.0013377 | 35 | 1050 | Unplanned | Unknown cause | Replace DDO fuses
55 |  | 3584-26 | Stout Street | Gisborne | Nelson 0803 | 2025-04-12 09:07 | 45759.3799 | 2025-04-12 10:48 | 45759.45 | 1.2391 | 0.012268 | 321 | 13484.9321 | Planned | Planned | Replace LA Standoffs
56 |  | 6015-26 | 1890 East Cape Road | Gisborne | Tiki Tiki 0206 | 2025-04-13 17:48 | 45760.7417 | 2025-04-13 18:48 | 45760.7833 | 0.032104 | 0.00053507 | 14 | 840 | Unplanned | Unknown cause | Replace DDO fuses
57 |  | 3595-26 | De Latour Rd | Gisborne | Crawford 1504 | 2025-04-14 10:07 | 45761.4215 | 2025-04-14 13:13 | 45761.5507 | 1.8625 | 0.010013 | 262 | 24609.9859 | Planned | Planned | Re-bed Streetlight pole cnr rutene Rd / De Lautour Rd
58 |  | 3606-26 | Marumoko road | Gisborne | Matawai 1204 | 2025-04-14 10:36 | 45761.4417 | 2025-04-14 15:50 | 45761.6597 | 0.024002 | 7.6438e-05 | 2 | 628 | Unplanned | Defective Equipment | Pole replacements completed. 1 x left for Tues 15/4 Generator left @ TX F120
59 |  | 3605-26 | 3962 SH2 Raupunga | Wairoa | Raupunga 3101 | 2025-04-14 11:10 | 45761.4653 | 2025-04-24 15:06 | 45771.6292 | 1.6781 | 0.00011466 | 3 | 43908 | Planned | Planned | Customer didn't require generation as no requirement onsite for power during the harvesting window. Power to be restored Thursday 17/4/25 (SW 3588B)
60 |  | 3574-26 | Raupunga | Wairoa | Raupunga 3101 | 2025-04-15 09:00 | 45762.375 | 2025-04-15 12:09 | 45762.5062 | 1.0379 | 0.0055418 | 145 | 13629.2414 | Planned | Planned | Tree cutting
61 |  | 3593-26 | Waiapu Road | Gisborne | Mata 0304 | 2025-04-15 09:02 | 45762.3764 | 2025-04-15 15:50 | 45762.6597 | 0.29627 | 0.00072616 | 19 | 3878.8146 | Planned | Planned | Replace HV poles
62 |  | 3606A-26 | Marumoko road | Gisborne | Matawai 1204 | 2025-04-15 09:19 | 45762.3882 | 2025-04-15 15:37 | 45762.6507 | 0.028894 | 7.6438e-05 | 2 | 756 | Unplanned | Defective Equipment | Replace HV Poles - Urgent work fault
63 |  | 6016-26 | 2270 Matawai Road | Gisborne | Te Karaka 1203 | 2025-04-15 20:36 | 45762.8583 | 2025-04-15 22:36 | 45762.9417 | 0.0091726 | 7.6438e-05 | 2 | 240 | Unplanned | Unknown cause | Replace DDO fuses
64 |  | 1777-26 | Rohepotae Road | Wairoa | Raupunga 3101 | 2025-04-16 12:25 | 45763.5174 | 2025-04-19 13:08 | 45766.5472 | 0.79029 | 0.0014523 | 38 | 20678 | Unplanned | Third Party Interference | Pole broken due to Highload contact LV W1742. Shock loading broke pole W5638
65 |  | 1779-26 | Hillside Road | Gisborne | Ngatapa 1102 | 2025-04-17 09:37 | 45764.4007 | 2025-04-17 13:11 | 45764.5493 | 0.016358 | 7.6438e-05 | 2 | 428 | Unplanned | Defective Equipment | Conductor broke between Poles D4928-D4929 - Rusty condition
66 |  | 6018-26 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-04-17 09:40 | 45764.4028 | 2025-04-17 10:40 | 45764.4444 | 0.0091726 | 0.00015288 | 4 | 240 | Unplanned | Unknown cause | Replace DDO fuses
67 |  | 1797-26 | Wharerata Road | Gisborne | Muriwai 0905 | 2025-04-17 17:11 | 45764.716 | 2025-04-17 19:55 | 45764.8299 | 0.84617 | 0.0051596 | 135 | 22140 | Unplanned | Vegetation | Tree through line C3503 - C3504
68 |  | 6017-26 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-04-17 19:43 | 45764.8215 | 2025-04-17 20:13 | 45764.8424 | 0.0045863 | 0.00015288 | 4 | 120 | Unplanned | Unknown cause | Replace DDO fuses
69 |  | 6019-26 | 1243 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-04-19 06:53 | 45766.2868 | 2025-04-19 08:53 | 45766.3701 | 0.18804 | 0.001567 | 41 | 4920 | Unplanned | Unknown cause | Replace DDO fuses
70 |  | 1798-26 | Tutamoe | Gisborne | Tauwhareparae 0404 | 2025-04-19 08:47 | 45766.366 | 2025-04-19 12:46 | 45766.5319 | 0.10048 | 0.00042041 | 11 | 2629 | Unplanned | Vegetation | Tree through line G1095
71 |  | 6020-26 | 636 Waiatai Valley Road | Wairoa | Nuhaka 3203 | 2025-04-19 09:56 | 45766.4139 | 2025-04-19 10:26 | 45766.4347 | 0.014905 | 0.00049685 | 13 | 390 | Unplanned | Unknown cause | Replace DDO fuses
72 |  | 6021-26 | 30 Renner Street | Gisborne | Lavenham 0902 | 2025-04-20 14:15 | 45767.5938 | 2025-04-20 15:15 | 45767.6354 | 0.016052 | 0.00026753 | 7 | 420 | Unplanned | Unknown cause | Replace DDO fuses
73 |  | 6022-26 | 10 Whitmore Road | Gisborne | Waimata 0903 | 2025-04-21 11:56 | 45768.4972 | 2025-04-21 12:56 | 45768.5389 | 0.018345 | 0.00030575 | 8 | 480 | Unplanned | Unknown cause | Replace DDO fuses
74 |  | 6023-26 | 697 Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-04-21 14:20 | 45768.5972 | 2025-04-21 18:50 | 45768.7847 | 0.020638 | 7.6438e-05 | 2 | 540 | Unplanned | Unknown cause | Replace DDO fuses
75 |  | 6024-26 | 5236 Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-04-22 13:50 | 45769.5764 | 2025-04-22 15:20 | 45769.6389 | 0.0034397 | 3.8219e-05 | 1 | 90 | Unplanned | Unknown cause | Replace DDO fuses
76 |  | 3596-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-04-23 08:32 | 45770.3556 | 2025-04-23 11:04 | 45770.4611 | 0.092949 | 0.0006115 | 16 | 1217.7611 | Planned | Planned | Tree Cutting
77 |  | 6025-26 | 1756 Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-04-24 08:57 | 45771.3729 | 2025-04-24 09:57 | 45771.4146 | 0.050449 | 0.00084082 | 22 | 1320 | Unplanned | Unknown cause | Replace DDO fuses
78 |  | 3588 C-26 | Arapata Road | Wairoa | Raupunga 3101 | 2025-04-24 09:04 | 45771.3778 | 2025-04-24 15:06 | 45771.6292 | 0.31821 | 0.00087904 | 23 | 8326 | Planned | Planned | Generator removed. Line breaks rejoined
79 |  | 6026-26 | 3059 Mahia East Coast Road | Wairoa | Mahia 3301 | 2025-04-24 11:15 | 45771.4688 | 2025-04-24 13:45 | 45771.5729 | 0.051596 | 0.00034397 | 9 | 1350 | Unplanned | Unknown cause | Replace DDO fuses
80 |  | 1782-26 | Hirini St, Wainui Rd, Rutene Rd, Esplanade, Ormond Rd,Peel St, Rawiri St | Gisborne | Esplanade 1503 | 2025-04-24 13:33 | 45771.5646 | 2025-04-28 16:12 | 45775.675 | 1.4537 | 0.031569 | 826 | 38037 | Unplanned | Defective Equipment | Cable termination failed @ RMS A333
81 |  | 3578-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-04-26 08:30 | 45773.3542 | 2025-04-26 13:54 | 45773.5792 | 0.24766 | 0.00076438 | 20 | 3242.4766 | Planned | Planned | Replace Poles
82 |  | 3578 A-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-04-26 08:30 | 45773.3542 | 2025-04-26 16:42 | 45773.6958 | 1.0906 | 0.0022167 | 58 | 14299.6279 | Planned | Planned | Replace Poles
83 |  | 1784-26 | Fox Street | Gisborne | Whangara 0506 | 2025-04-26 10:28 | 45773.4361 | 2025-04-26 12:25 | 45773.5174 | 1.286 | 0.022549 | 590 | 33648 | Unplanned | Vegetation | Tree Contact
84 |  | 1785-26 | Mangapoike | Wairoa | Frasertown 3103 | 2025-04-27 07:31 | 45774.3132 | 2025-04-27 10:26 | 45774.4347 | 0.47487 | 0.0027135 | 71 | 12425 | Unplanned | Wildlife | Bird strike, broke conductor
85 |  | 3579-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-04-28 08:30 | 45775.3542 | 2025-04-28 15:52 | 45775.6611 | 0.946 | 0.0021403 | 56 | 12402.4879 | Planned | Planned | Replace HV poles
86 |  | 3599-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-04-29 08:30 | 45776.3542 | 2025-04-29 16:00 | 45776.6667 | 0.61915 | 0.0013759 | 36 | 8111.1447 | Planned | Planned | Replace HV poles
87 |  | 3598-26 | Hereheretau Road | Wairoa | Nuhaka 3203 | 2025-04-29 09:03 | 45776.3771 | 2025-04-29 16:18 | 45776.6792 | 0.31588 | 0.00072616 | 19 | 3964.3767 | Planned | Planned | Replace TX W490
88 |  | 1787-26 | Waiomoko Road | Gisborne | Dalton 0502 | 2025-04-29 09:57 | 45776.4146 | 2025-04-29 11:44 | 45776.4889 | 0.036805 | 0.00034397 | 9 | 963 | Unplanned | Wildlife | Bird found @ base of pole
89 |  | 1788-26 | Harrington Road | Gisborne | Te Arai 0906 | 2025-04-29 17:47 | 45776.741 | 2025-04-29 18:58 | 45776.7903 | 0.013568 | 0.00019109 | 5 | 355 | Unplanned | Wildlife | Bird contact centre ph to arm, burnt x-arm
90 |  | 3600 A-26 | Te Araroa Rd, Waione Rd | Gisborne | Awatere 0101 | 2025-05-01 08:32 | 45778.3556 | 2025-05-01 15:31 | 45778.6465 | 0.5765 | 0.0013759 | 36 | 7552.3769 | Planned | Planned | Replace HV Poles
91 |  | 3613-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2025-05-01 13:00 | 45778.5417 | 2025-05-01 13:37 | 45778.5674 | 0.014141 | 0.00038219 | 10 | 185.0707 | Planned | Planned | Install new HV fuses D3663 & TX D6720
92 |  | 1789-26 | Mata Road | Gisborne | Mata 0304 | 2025-05-01 18:38 | 45778.7764 | 2025-05-02 12:40 | 45779.5278 | 0.95372 | 0.0011466 | 30 | 24954 | Unplanned | Defective Equipment | Conductor broke at binder - Pole H1009
93 |  | 1790-26 | Hillside Road | Gisborne | Ngatapa 1102 | 2025-05-02 07:27 | 45779.3104 | 2025-05-02 11:28 | 45779.4778 | 0.018422 | 7.6438e-05 | 2 | 482 | Unplanned | Defective Equipment | Conductor 07/16 Steel - rotten and failing
94 |  | 3607-26 | Matawai Road | Gisborne | Bushmere 0805 | 2025-05-02 09:01 | 45779.3757 | 2025-05-02 10:44 | 45779.4472 | 0.22832 | 0.0022167 | 58 | 2993.6213 | Planned | Planned | Replace DDO holders @ HV links D4318
95 |  | 3601-26 | Ruakituri | Wairoa | Ruakituri 2003 | 2025-05-02 10:49 | 45779.4507 | 2025-05-02 14:14 | 45779.5931 | 0.62679 | 0.0030575 | 80 | 8236.6902 | Planned | Planned | Replace 11kV pole W1803
96 |  | 6027-26 | 463 Lake Road | Gisborne | Lavenham 0902 | 2025-05-05 06:35 | 45782.2743 | 2025-05-05 08:00 | 45782.3333 | 0.019492 | 0.00022931 | 6 | 510 | Unplanned | Wildlife | Bird strike, replace fuses
97 |  | 6028-26 | 1400 Wharerata Road | Gisborne | Muriwai 0905 | 2025-05-05 13:35 | 45782.566 | 2025-05-05 14:00 | 45782.5833 | 0.00095547 | 3.8219e-05 | 1 | 25 | Unplanned | Wildlife | Bird strike, replace fuses
98 |  | 1793-26 | Waimata Valley | Gisborne | Waimata 0903 | 2025-05-06 06:46 | 45783.2819 | 2025-05-06 14:00 | 45783.5833 | 0.40462 | 0.0058475 | 153 | 10587 | Unplanned | Vegetation | Tree fell on the line between pole G211 - G212
99 |  | 3608-26 | Waione Road | Gisborne | Awatere 0101 | 2025-05-06 08:30 | 45783.3542 | 2025-05-06 16:08 | 45783.6722 | 0.63015 | 0.0013759 | 36 | 8111.1447 | Planned | Planned | Replace Poles
100 |  | 3604-26 | Kaimoe road | Gisborne | Lavenham 0902 | 2025-05-06 09:07 | 45783.3799 | 2025-05-06 10:01 | 45783.4174 | 0.13208 | 0.002446 | 64 | 1732.6964 | Planned | Planned | Install new TX for sections
101 |  | 3624-26 | Fox Street | Gisborne | Whangara 0506 | 2025-05-06 12:05 | 45783.5035 | 2025-05-06 16:48 | 45783.7 | 1.9252 | 0.006803 | 178 | 50374 | Planned | Planned | To clear trees & vegetation
102 |  | 1794-26 | Waiotu Road | Gisborne | Mata 0304 | 2025-05-06 22:18 | 45783.9292 | 2025-05-07 10:26 | 45784.4347 | 0.85844 | 0.013759 | 360 | 22461 | Unplanned | Wildlife | Conductor broken between poles H2544 - H2545
103 |  | 1795-26 | Gordon Road | Gisborne | Te Arai 0906 | 2025-05-07 07:40 | 45784.3194 | 2025-05-07 10:27 | 45784.4354 | 0.076591 | 0.00045863 | 12 | 2004 | Unplanned | Defective Equipment | Repair broken HV conductor between poles C361 - C2738
104 |  | 3621-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-05-07 08:30 | 45784.3542 | 2025-05-07 13:31 | 45784.5632 | 0.64422 | 0.0021403 | 56 | 16856 | Planned | Planned | Replace Poles
105 |  | 6029-26 | 264 Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-05-07 16:08 | 45784.6722 | 2025-05-07 18:20 | 45784.7639 | 0.01009 | 7.6438e-05 | 2 | 264 | Unplanned | Unknown cause | Replace fuses
106 |  | 3609-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-05-08 08:30 | 45785.3542 | 2025-05-08 13:19 | 45785.5549 | 0.39763 | 0.0013759 | 36 | 5210.1727 | Planned | Planned | Replace Poles
107 |  | 3589 A-26 | Whangara Road | Gisborne | Dalton 0502 | 2025-05-08 08:33 | 45785.3562 | 2025-05-08 14:09 | 45785.5896 | 0.4623 | 0.0013759 | 36 | 12096 | Planned | Planned | Replace Poles
108 |  | 6030-26 | 121 Beach Road | Gisborne | Tiki Tiki 0206 | 2025-05-08 17:04 | 45785.7111 | 2025-05-08 18:59 | 45785.791 | 0.0043952 | 3.8219e-05 | 1 | 115 | Unplanned | Adverse Weather | Replaced burnt out HV tube + 2amp link + 1 x 63amp dinoo hrc
109 |  | 1801-26 | Waimatatini Road | Gisborne | Tiki Tiki 0206 | 2025-05-09 04:21 | 45786.1813 | 2025-05-09 11:31 | 45786.4799 | 0.28412 | 0.0019874 | 52 | 7434 | Unplanned | Defective Equipment | Replaced HV fuses at TX J267
110 |  | 3610-26 | Whakaangiangi | Gisborne | Awatere 0101 | 2025-05-09 08:30 | 45786.3542 | 2025-05-09 13:12 | 45786.55 | 0.35567 | 0.0012612 | 33 | 4659.8674 | Planned | Planned | Replace Poles
111 |  | 6031-26 | 2987 Mata Road | Gisborne | Mata 0304 | 2025-05-09 09:55 | 45786.4132 | 2025-05-09 11:08 | 45786.4639 | 0.00558 | 7.6438e-05 | 2 | 146 | Unplanned | Unknown cause | Replace fuses
112 |  | 6032-26 | 1370 Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2025-05-09 15:57 | 45786.6646 | 2025-05-09 17:50 | 45786.7431 | 0.012956 | 0.00011466 | 3 | 339 | Unplanned | Adverse Weather | Heavy rain / winds
113 |  | 6033-26 | 184 Awanui Road | Gisborne | Tiki Tiki 0206 | 2025-05-10 07:44 | 45787.3222 | 2025-05-11 11:32 | 45788.4806 | 0.1275 | 7.6438e-05 | 2 | 3336 | Unplanned | Defective Equipment | Faulty glass fuse holder, kept arcing when replaced. Replaced all 3 glass bases for new 11th
114 |  | 6034-25 | 41 Te Hue Road | Gisborne | Awatere 0101 | 2025-05-10 09:23 | 45787.391 | 2025-05-10 11:29 | 45787.4785 | 0.0096312 | 7.6438e-05 | 2 | 252 | Unplanned | Adverse Weather | First 2 fuses blew when putting 2nd fuse in. Held 2nd time after line patrol
115 |  | 1803-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-05-10 09:55 | 45787.4132 | 2025-05-11 15:00 | 45788.625 | 0.13338 | 7.6438e-05 | 2 | 3490 | Unplanned | Adverse Environment | Tree brought down through HV lines due to landslip
116 |  | 6035-26 | 1048 Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-05-10 09:55 | 45787.4132 | 2025-05-11 15:26 | 45788.6431 | 0.13537 | 7.6438e-05 | 2 | 3542 | Unplanned | Vegetation | Replace fuses
117 |  | 1802-26 | Tamarau Feeder | Gisborne | Tamarau 0503 | 2025-05-10 20:25 | 45787.8507 | 2025-05-11 14:59 | 45788.6243 | 2.3217 | 0.041697 | 1091 | 60748 | Unplanned | Third Party Interference | Car V's Pole
118 |  | 6036-26 | 1379 Moanui road | Gisborne | Matawai 1204 | 2025-05-12 07:44 | 45789.3222 | 2025-05-12 23:45 | 45789.9896 | 0.18364 | 0.00019109 | 5 | 4805 | Unplanned | Wildlife | Replace fuses
119 |  | 3614-26 | Pakowhai Road | Gisborne | Muriwai 0905 | 2025-05-12 09:02 | 45789.3764 | 2025-05-12 14:36 | 45789.6083 | 0.20424 | 0.0006115 | 16 | 2673.6339 | Planned | Planned | Replace poles
120 |  | 3611-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-05-12 09:10 | 45789.3819 | 2025-05-12 14:51 | 45789.6188 | 0.38907 | 0.00279 | 73 | 2853.6676 | Planned | Planned | Install Genset @ TX G53 & G234. Drop HV conductor Poles G2061 - G2060
121 |  | 3611-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-05-12 09:10 | 45789.3819 | 2025-05-12 14:51 | 45789.6188 | 0.010319 | 7.6438e-05 | 2 | 270 | Unplanned | Human Error | Missed advertising from planned job
122 |  | 6037-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-05-12 20:21 | 45789.8479 | 2025-05-12 21:10 | 45789.8819 | 0.013109 | 0.00026753 | 7 | 343 | Unplanned | Wildlife | Replace fuses
123 |  | 1805-26 | Tauwhareparae Rd, Fernside Rd, Matanui Rd | Gisborne | Tauwhareparae 0404 | 2025-05-13 02:51 | 45790.1188 | 2025-05-13 12:55 | 45790.5382 | 0.57711 | 0.00095547 | 25 | 15100 | Unplanned | Defective Equipment | 100kVA genset failed on over frequency runaway
124 |  | 6038-26 | 581 Waihau Road | Gisborne | Rototahi 0403 | 2025-05-13 08:11 | 45790.341 | 2025-05-13 12:22 | 45790.5153 | 0.1343 | 0.00053507 | 14 | 3514 | Unplanned | Unknown cause | Replace fuses
125 |  | 3615-26 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2025-05-13 09:02 | 45790.3764 | 2025-05-13 15:36 | 45790.65 | 0.7228 | 0.0018345 | 48 | 9473.3471 | Planned | Planned | Dismantle HV lines for tree cutting
126 |  | 1806-26 | 932 Awamate Road | Wairoa | Frasertown 3103 | 2025-05-14 12:49 | 45791.534 | 2025-05-14 13:56 | 45791.5806 | 0.010243 | 0.00015288 | 4 | 268 | Unplanned | Defective Equipment | Replace TX W1641. Oil leak was apparent
127 |  | 3612-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-05-14 14:02 | 45791.5847 | 2025-05-14 14:55 | 45791.6215 | 0.098299 | 0.0018727 | 49 | 1287.2044 | Planned | Planned | Restore HV conductor. Poles G2061-G2060. Remove generators @ TX G53 & TX G234
128 |  | 6039-26 | 466 Manders Road | Gisborne | Waimata 0903 | 2025-05-14 14:10 | 45791.5903 | 2025-05-14 16:30 | 45791.6875 | 0.10166 | 0.00072616 | 19 | 2660 | Unplanned | Unknown cause | Replace fuses
129 |  | 6040-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-05-14 17:15 | 45791.7188 | 2025-05-14 18:05 | 45791.7535 | 0.013377 | 0.00026753 | 7 | 350 | Unplanned | Unknown cause | Replace fuses
130 |  | 3616-26 | Waiapu Road | Gisborne | Mata 0304 | 2025-05-15 09:00 | 45792.375 | 2025-05-15 12:27 | 45792.5188 | 0.11867 | 0.00057328 | 15 | 1553.7899 | Planned | Planned | Replace HV Poles
131 |  | 1807-26 | Maraehara Road | Gisborne | Tiki Tiki 0206 | 2025-05-16 08:40 | 45793.3611 | 2025-05-16 10:51 | 45793.4521 | 0.1502 | 0.0011466 | 30 | 3930 | Unplanned | Wildlife | Repair HV conductor between poles J2202 - J2203 - Bird strike
132 |  | 1848-26 | Kakaniki, Waiomatatini | Gisborne | Tiki Tiki 0206 | 2025-05-16 20:32 | 45793.8556 | 2025-05-17 08:46 | 45794.3653 | 0.92322 | 0.0097076 | 254 | 24156 | Unplanned | Wildlife | Broken conductor by Bird strike
133 |  | 6041-26 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-05-17 07:20 | 45794.3056 | 2025-05-17 10:00 | 45794.4167 | 0.02446 | 0.00015288 | 4 | 640 | Unplanned | Unknown cause | Replace fuses
134 |  | 6042-26 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-05-17 10:24 | 45794.4333 | 2025-05-17 12:04 | 45794.5028 | 0.015288 | 0.00015288 | 4 | 400 | Unplanned | Unknown cause | Replace fuses
135 |  | 3617-26 | Back Ormond Road | Gisborne | Nelson 0803 | 2025-05-20 09:03 | 45797.3771 | 2025-05-20 11:08 | 45797.4639 | 0.13854 | 0.0011084 | 29 | 1814.5089 | Planned | Planned | Replace TX C1528 with 3ph TX
136 |  | 6043-26 | 157 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2025-05-21 06:58 | 45798.2903 | 2025-05-21 08:10 | 45798.3403 | 0.0055035 | 7.6438e-05 | 2 | 144 | Unplanned | Wildlife | Possum contacted HV glass fuse
137 |  | 3637-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-05-21 09:02 | 45798.3764 | 2025-05-21 10:49 | 45798.4507 | 0.07361 | 0.00068794 | 18 | 1926 | Planned | Planned | Resag HV conductor @ Pole J2403
138 |  | 3618-26 | Fitzroy Street | Wairoa | Borough Two 3205 | 2025-05-21 09:03 | 45798.3771 | 2025-05-21 13:42 | 45798.5708 | 0.095968 | 0.00034397 | 9 | 1255.9644 | Planned | Planned | Install new pole , midspan W1588 - W948
139 |  | 3622-26 | Darwin Road | Gisborne | Whangara 0506 | 2025-05-21 09:04 | 45798.3778 | 2025-05-21 11:58 | 45798.4986 | 1.1505 | 0.0066119 | 173 | 7488.1858 | Planned | Planned | Chorus pole change betwn Poles A4176 - A4058
140 |  | 3627-26 | Oakview Subdivision | Gisborne | Nelson 0803 | 2025-05-21 09:05 | 45798.3785 | 2025-05-21 10:38 | 45798.4431 | 0.12796 | 0.0013759 | 36 | 1678.4579 | Planned | Planned | Identify & Lebel LV runs TX C420. Additional phase added to DB 13180
141 |  | 3630-26 | Atkinson Street | Gisborne | Gladstone 0607 | 2025-05-22 08:33 | 45799.3562 | 2025-05-22 11:38 | 45799.4847 | 0.69998 | 0.0037837 | 99 | 9192.1491 | Planned | Planned | Replace pole B2220
142 |  | 3623-26 | Waihinahina Way | Wairoa | Mahia 3301 | 2025-05-22 09:09 | 45799.3812 | 2025-05-22 13:01 | 45799.5424 | 0.035467 | 0.00015288 | 4 | 462.0706 | Planned | Planned | Upgrade 400V TX W1095
143 |  | 1811-26 | Arakihi road | Gisborne | Tauwhareparae 0404 | 2025-05-22 12:19 | 45799.5132 | 2025-05-22 13:23 | 45799.5576 | 0.056258 | 0.00087904 | 23 | 1472 | Unplanned | Defective Equipment | Faulty HV fuses at TX G141
144 |  | 3629-26 | Scott Street | Gisborne | Chalmers 0707 | 2025-05-23 08:32 | 45800.3556 | 2025-05-23 09:05 | 45800.3785 | 0.094592 | 0.0028664 | 75 | 1241.0472 | Planned | Planned | Replace 11kV insulators
145 |  | 3632 A-26 | Mangaroa Road | Wairoa | Ruakituri 2003 | 2025-05-23 08:47 | 45800.366 | 2025-05-23 15:57 | 45800.6646 | 0.083623 | 0.00038219 | 10 | 1081.2901 | Planned | Planned | Replace Pole W1803
146 |  | 6044-26 | 564 Centennial Marine Drive | Gisborne | JNL_A 1405 | 2025-05-24 06:49 | 45801.284 | 2025-05-24 08:00 | 45801.3333 | 0.016281 | 0.00022931 | 6 | 426 | Unplanned | Unknown cause | Replace fuses
147 |  | 6045-26 | 57 Pitcher Road | Gisborne | Te Karaka 1203 | 2025-05-25 11:36 | 45802.4833 | 2025-05-25 12:05 | 45802.5035 | 0.0077585 | 0.00026753 | 7 | 203 | Unplanned | Wildlife | Replace fuses
148 |  | 6046-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-05-25 16:06 | 45802.6708 | 2025-05-25 16:30 | 45802.6875 | 0.0064208 | 0.00026753 | 7 | 168 | Unplanned | Unknown cause | Replace fuses
149 |  | 6047-26 | 1809 Matawai Road | Gisborne | Te Karaka 1203 | 2025-05-26 15:02 | 45803.6264 | 2025-05-26 16:30 | 45803.6875 | 0.013453 | 0.00015288 | 4 | 352 | Unplanned | Vegetation | Replace fuses
150 |  | 3619-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-05-27 08:33 | 45804.3562 | 2025-05-27 13:35 | 45804.566 | 0.18467 | 0.0006115 | 16 | 2417.7611 | Planned | Planned | Tree Cutting
151 |  | 1813-26 | Matawai | Gisborne | Matawai 1204 | 2025-05-28 05:55 | 45805.2465 | 2025-05-29 17:26 | 45806.7264 | 16.1202 | 0.055991 | 1465 | 421784 | Unplanned | Unknown cause | Intermittent earth fault at start of line. Not found. Acostic dish used next day and nothing found
152 |  | 3634-26 | Kitchener Street | Wairoa | Brickworks 3201 | 2025-05-28 08:03 | 45805.3354 | 2025-05-28 18:08 | 45805.7556 | 1.2717 | 0.002102 | 55 | 14798.5419 | Planned | Planned | Upgrade SDAF3 to CFCF RMU
153 |  | 3620-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-05-28 08:32 | 45805.3556 | 2025-05-28 15:28 | 45805.6444 | 0.25439 | 0.0006115 | 16 | 3330.0351 | Planned | Planned | Tree removal
154 |  | 1815-26 | Ormond Road | Gisborne | Te Karaka 1203 | 2025-05-28 20:05 | 45805.8368 | 2025-05-28 22:10 | 45805.9236 | 0.9189 | 0.0097076 | 254 | 24043 | Unplanned | Vegetation | Branch on line E91 - E1848
155 |  | 1814-26 | Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2025-05-28 20:08 | 45805.8389 | 2025-05-28 22:34 | 45805.9403 | 0.14324 | 0.00099369 | 26 | 3748 | Unplanned | Adverse Weather | High winds caused clashing. Line reclosed back in.
156 |  | 1816-26 | Whakaangiangi Road / Te Araroa Rd | Gisborne | Awatere 0101 | 2025-05-28 20:35 | 45805.8576 | 2025-05-28 21:45 | 45805.9062 | 0.11011 | 0.0034779 | 91 | 2881 | Unplanned | Adverse Weather | High winds caused line clashing. Fault went back in.
157 |  | 1817-26 | Tolaga | Gisborne | Toko Tie 0401 | 2025-05-29 08:32 | 45806.3556 | 2025-05-29 08:48 | 45806.3667 | 0.051978 | 0.0032486 | 85 | 1360 | Unplanned | Unknown cause | 50kV trip A8 cause unknown - flew line
158 |  | 1817-26 | Tolaga | Gisborne | Town 0402 | 2025-05-29 08:32 | 45806.3556 | 2025-05-29 08:48 | 45806.3667 | 0.12414 | 0.0077585 | 203 | 3248 | Unplanned | Unknown cause | 50kV trip A8 cause unknown - flew line
159 |  | 1817-26 | Tolaga | Gisborne | Tauwhareparae 0404 | 2025-05-29 08:32 | 45806.3556 | 2025-05-29 08:48 | 45806.3667 | 0.086834 | 0.0054271 | 142 | 2272 | Unplanned | Unknown cause | 50kV trip A8 cause unknown - flew line
160 |  | 1817-26 | Tolaga | Gisborne | Rototahi 0403 | 2025-05-29 08:32 | 45806.3556 | 2025-05-29 08:48 | 45806.3667 | 0.12169 | 0.0076056 | 199 | 3184 | Unplanned | Unknown cause | 50kV trip A8 cause unknown - flew line
161 |  | 1817-26 | Tolaga | Gisborne | Tolaga Bay LS 0420 | 2025-05-29 08:32 | 45806.3556 | 2025-05-29 08:48 | 45806.3667 | 0.0006115 | 3.8219e-05 | 1 | 16 | Unplanned | Unknown cause | 50kV trip A8 cause unknown - flew line
162 |  | 3633-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-05-29 08:35 | 45806.3576 | 2025-05-29 13:43 | 45806.5715 | 0.18834 | 0.0006115 | 16 | 2465.7611 | Planned | Planned | Replace HV Poles
163 |  | 3628-26 | Wharekopae Road | Gisborne | Ngatapa 1102 | 2025-05-30 09:01 | 45807.3757 | 2025-05-30 10:44 | 45807.4472 | 0.01181 | 0.00011466 | 3 | 309 | Planned | Planned | Replace 11kV Poles
164 |  | 3653-26 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2025-05-30 09:04 | 45807.3778 | 2025-05-30 12:35 | 45807.5243 | 0.056449 | 0.00026753 | 7 | 1477 | Planned | Planned | Emergency isolation for Tree cutting
165 |  | 3635-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-05-30 09:07 | 45807.3799 | 2025-05-30 13:54 | 45807.5792 | 0.38391 | 0.0013377 | 35 | 5030.225 | Planned | Planned | Replace HV poles
166 |  | 1818-26 | Papatu Road | Gisborne | Muriwai 0905 | 2025-05-30 11:51 | 45807.4938 | 2025-05-30 12:37 | 45807.5257 | 0.050984 | 0.0011084 | 29 | 1334 | Unplanned | Human Error | Tree brush through 11kv Lines at pole C1338 & HV fuses C1310 operated
167 |  | 3636-26 | Roebuck Road | Gisborne | Childers 0605 | 2025-05-31 09:01 | 45808.3757 | 2025-05-31 13:01 | 45808.5424 | 0.045863 | 0.00019109 | 5 | 600.1147 | Planned | Planned | Replace LV Rack
168 |  | 1819-26 | Tikitiki | Gisborne | Tiki Tiki 0206 | 2025-05-31 15:43 | 45808.6549 | 2025-05-31 18:11 | 45808.7576 | 0.54714 | 0.012001 | 314 | 14316 | Unplanned | Wildlife | To repair broken 11kV line between Pole J378 - J815 due to bird strike
169 |  | 6048A-26 | 183 Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-02 09:24 | 45810.3917 | 2025-06-02 11:30 | 45810.4792 | 0.10594 | 0.00084082 | 22 | 2772 | Unplanned | Vegetation | Replaced fuses
170 |  | 6049A-26 | 641 Mata Road | Gisborne | Mata 0304 | 2025-06-04 06:34 | 45812.2736 | 2025-06-04 07:45 | 45812.3229 | 0.010854 | 0.00015288 | 4 | 284 | Unplanned | Unknown cause | Replace fuses - Gusty winds
171 |  | 3638-26 | Waione Road | Gisborne | Awatere 0101 | 2025-06-04 08:30 | 45812.3542 | 2025-06-04 14:28 | 45812.6028 | 0.49257 | 0.0013759 | 36 | 6452.8662 | Planned | Planned | Replace Poles
172 |  | 3640-26 | Kitchener St / McLean St | Wairoa | Brickworks 3201 | 2025-06-04 08:34 | 45812.3569 | 2025-06-04 17:48 | 45812.7417 | 1.2916 | 0.0023314 | 61 | 15468.9799 | Planned | Planned | Raise existing RMU W297 / W298 / W299
173 |  | 1828-26 | Tahora Rd, Wharekopae Rd | Gisborne | Tahora 1103 | 2025-06-04 08:45 | 45812.3646 | 2025-06-06 15:41 | 45814.6535 | 3.0605 | 0.0028664 | 75 | 80078 | Unplanned | Defective Equipment | TX Pole D541 rotten @ ground level
174 |  | 3661-26 | Barkers Hill Road | Gisborne | Aberdeen 0609 | 2025-06-04 09:03 | 45812.3771 | 2025-06-04 15:49 | 45812.659 | 1.412 | 0.0034779 | 91 | 36946 | Planned | Planned | Clear trees Pole B1154
175 |  | 1823-26 | Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2025-06-04 15:46 | 45812.6569 | 2025-06-05 14:20 | 45813.5972 | 0.62801 | 0.0023696 | 62 | 16432 | Unplanned | Adverse Environment | Broken 11kV line between Pole J2904-J2907 which caused by adverse weather (flooding) in the area
176 |  | 1824-26 | Waihi Road | Wairoa | Frasertown 3103 | 2025-06-04 15:46 | 45812.6569 | 2025-06-07 17:02 | 45815.7097 | 1.2765 | 0.008905 | 233 | 33400 | Unplanned | Defective Equipment | Replace broken pole W3683 - Repair conductor
177 |  | 1827-26 | Raupunga | Wairoa | Raupunga 3101 | 2025-06-04 17:13 | 45812.7174 | 2025-06-04 17:36 | 45812.7333 | 0.082897 | 0.0060004 | 157 | 2169 | Unplanned | Adverse Weather | Suspected line clash due to strong wind
178 |  | 1825-26 | Whakarau Road | Gisborne | Matawai 1204 | 2025-06-04 17:44 | 45812.7389 | 2025-06-11 11:50 | 45819.4931 | 2.1464 | 0.0027135 | 71 | 56160 | Unplanned | Defective Equipment | HV conductor down between F2283 - F2282
179 |  | 1826a-26 | Onepoto/Kokako | Wairoa | Village 2002 | 2025-06-04 20:22 | 45812.8486 | 2025-06-05 09:54 | 45813.4125 | 1.6758 | 0.0020638 | 54 | 43848 | Unplanned | Adverse Weather | Lines clashing in wind during storm. Outage found as part of private fault 1826.
180 |  | 1835-26 | Raupunga | Wairoa | Raupunga 3101 | 2025-06-04 20:46 | 45812.8653 | 2025-06-04 21:10 | 45812.8819 | 0.10201 | 0.0065354 | 171 | 2669 | Unplanned | Adverse Weather | Windy conditions
181 |  | 1830-26 | Hiriroa Rd South / Totangi Road | Gisborne | Totangi 1101 | 2025-06-05 01:42 | 45813.0708 | 2025-06-05 19:25 | 45813.809 | 0.47724 | 0.00053507 | 14 | 12487 | Unplanned | Adverse Weather | No obvious fault located - High winds
182 |  | 1829-26 | Marumoko Road | Gisborne | Matawai 1204 | 2025-06-05 01:43 | 45813.0715 | 2025-06-08 13:35 | 45816.566 | 2.3227 | 0.0043952 | 115 | 60773 | Unplanned | Defective Equipment | Pole down @ F2412. Access constraints due to flooding @ bridge / Helicopter access. Note pole was originally reported as F2413.
183 |  | 1831-26 | Raupunga | Wairoa | Raupunga 3101 | 2025-06-05 08:13 | 45813.3424 | 2025-06-09 16:51 | 45817.7021 | 4.2969 | 0.030843 | 807 | 112428 | Unplanned | Defective Equipment | Waireka beyond W1024 - broken binder at Pole W3700
184 |  | 1836-26 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2025-06-05 09:08 | 45813.3806 | 2025-06-06 14:25 | 45814.6007 | 0.7382 | 0.00042041 | 11 | 19315 | Unplanned | Adverse Weather | Line clash due to wind
185 |  | 1833-26 | Waingake Rd, Tawera Rd, Paparatu Rd | Gisborne | Te Arai 0906 | 2025-06-05 10:13 | 45813.4257 | 2025-06-08 15:29 | 45816.6451 | 1.5663 | 0.0031722 | 83 | 40981 | Unplanned | Vegetation | Trees through line @ pole C789
186 |  | 1834-26 | Mangahaumi Road | Gisborne | Whatatutu 1201 | 2025-06-05 11:10 | 45813.4653 | 2025-06-05 12:44 | 45813.5306 | 0.089815 | 0.00095547 | 25 | 2350 | Unplanned | Vegetation | Trees touching line
187 |  | 1832-26 | Crosshill | Wairoa | Ruakituri 2003 | 2025-06-05 11:32 | 45813.4806 | 2025-06-05 20:49 | 45813.8674 | 1.0847 | 0.0019492 | 51 | 28380 | Unplanned | Vegetation | Pole W7316 broken (beyond W818) - Caused by Tree coming down in wind. Note - this fault was found after the whole feeder tripped in private fault 1826. The start time follows on from the relevant line in 1826, and starts when we began work on clearing the tree from the line (11.32am).
188 |  | 3644-26 | East Cape Road | Gisborne | Te Araroa 0103 | 2025-06-06 08:30 | 45814.3542 | 2025-06-06 09:21 | 45814.3896 | 0.042576 | 0.00084082 | 22 | 557.9264 | Planned | Planned | Install TX
189 |  | 1839-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-06-06 11:08 | 45814.4639 | 2025-06-06 13:25 | 45814.559 | 0.010472 | 7.6438e-05 | 2 | 274 | Unplanned | Vegetation | Tree through 11kV line between pole J3043-J3044
190 |  | 1842-26 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2025-06-06 15:49 | 45814.659 | 2025-06-13 12:25 | 45821.5174 | 0.61842 | 0.00084082 | 22 | 16181 | Unplanned | Defective Equipment | Wire down between Pole D3770 - D3768
191 |  | 1841-26 | Te Wera Road, Koranga Valley Road | Gisborne | Matawai 1204 | 2025-06-06 16:24 | 45814.6833 | 2025-06-06 17:38 | 45814.7347 | 0.073533 | 0.00099369 | 26 | 1924 | Unplanned | Defective Equipment | Redundant LV conductor across HV line - LV cleared - HV Restored
192 |  | 1844-26 | Whakaangiangi | Gisborne | Awatere 0101 | 2025-06-07 10:09 | 45815.4229 | 2025-06-07 12:14 | 45815.5097 | 0.0095547 | 7.6438e-05 | 2 | 250 | Unplanned | Vegetation | Trees on line
193 |  | 1845-26 | Te Araroa Road, Lotton Point, Waikura | Gisborne | Hicks Bay 0102 | 2025-06-07 13:34 | 45815.5653 | 2025-06-11 11:06 | 45819.4625 | 1.3598 | 0.0058475 | 153 | 35580 | Unplanned | Defective Equipment | HV insulator floating off pole J4478. Conductor broke
194 |  | 6050A-26 | 100 Cameron Road | Gisborne | Nelson 0803 | 2025-06-07 20:51 | 45815.8688 | 2025-06-07 22:30 | 45815.9375 | 0.060539 | 0.0006115 | 16 | 1584 | Unplanned | Unknown cause | Replaced fuses
195 |  | 1843-26 | Lake Road | Wairoa | Frasertown 3103 | 2025-06-08 09:13 | 45816.384 | 2025-06-08 10:04 | 45816.4194 | 0.099064 | 0.0019874 | 52 | 2592 | Unplanned | Defective Equipment | Repair HV Jumper TX W1674. Replace HV insulator Pole W4824
196 |  | 1847-26 | Mangatokerau Road | Gisborne | Toko Tie 0401 | 2025-06-08 15:17 | 45816.6368 | 2025-06-10 12:39 | 45818.5271 | 0.11928 | 0.00019109 | 5 | 3121 | Unplanned | Vegetation | Tree brought down wire across river from Pole G1664 & G292. HV jumpers cut away, then repaired
197 |  | 6051A-26 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2025-06-09 04:58 | 45817.2069 | 2025-06-09 09:40 | 45817.4028 | 0.15089 | 0.00053507 | 14 | 3948 | Unplanned | Unknown cause | Replaced fuses
198 |  | 6052A-26 | 5900 Te Araroa Road, Hicks Bay | Gisborne | Hicks Bay 0102 | 2025-06-09 13:38 | 45817.5681 | 2025-06-09 15:45 | 45817.6562 | 0.0097076 | 7.6438e-05 | 2 | 254 | Unplanned | Unknown cause | Replaced fuses
199 |  | 6053A-26 | 1000 Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-06-09 17:51 | 45817.7438 | 2025-06-09 23:44 | 45817.9889 | 0.29681 | 0.00084082 | 22 | 7766 | Unplanned | Adverse Weather | Replaced fuses
200 |  | 6054A-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-10 09:01 | 45818.3757 | 2025-06-10 11:15 | 45818.4688 | 0.035849 | 0.00026753 | 7 | 938 | Unplanned | Wildlife | Replaced fuses
201 |  | 6055A-26 | 97 Waiomoko Road | Gisborne | Dalton 0502 | 2025-06-10 17:08 | 45818.7139 | 2025-06-10 18:57 | 45818.7896 | 0.087483 | 0.0008026 | 21 | 2289 | Unplanned | Lightning | Replaced fuses
202 |  | 6056A-26 | 503 Lake Road | Gisborne | Lavenham 0902 | 2025-06-11 04:49 | 45819.2007 | 2025-06-11 14:50 | 45819.6181 | 0.13782 | 0.00022931 | 6 | 3606 | Unplanned | Lightning | Replaced fuses
203 |  | 6057A-26 | 1354 Matawai Road | Gisborne | Waimata 0903 | 2025-06-11 07:23 | 45819.3076 | 2025-06-11 08:25 | 45819.3507 | 0.0047392 | 7.6438e-05 | 2 | 124 | Unplanned | Lightning | Replaced fuses
204 |  | 6058A-26 | 864 Lavenham Road | Gisborne | Lavenham 0902 | 2025-06-11 08:01 | 45819.334 | 2025-06-11 12:50 | 45819.5347 | 0.011045 | 3.8219e-05 | 1 | 289 | Unplanned | Lightning | Replaced fuses
205 |  | 3647-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-11 09:01 | 45819.3757 | 2025-06-11 14:05 | 45819.5868 | 0.61578 | 0.0020256 | 53 | 8073.7139 | Planned | Planned | Replace HV Poles - Remove ABS J165
206 |  | 6059A-26 | 1406 Matawai Road | Gisborne | Waimata 0903 | 2025-06-11 13:24 | 45819.5583 | 2025-06-11 15:00 | 45819.625 | 0.003669 | 3.8219e-05 | 1 | 96 | Unplanned | Unknown cause | Replaced fuses
207 |  | 6060A-26 | 1107 Riverside Road | Gisborne | Waimata 0903 | 2025-06-11 14:23 | 45819.5993 | 2025-06-11 16:30 | 45819.6875 | 0.024269 | 0.00019109 | 5 | 635 | Unplanned | Unknown cause | Replaced fuses
208 |  | 1853-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-06-11 16:09 | 45819.6729 | 2025-06-12 12:56 | 45820.5389 | 0.29669 | 0.00030575 | 8 | 7763 | Unplanned | Vegetation | HV conductor brought down by tree - E1132-E1131
209 |  | 6061A-26 | 31 Humphreys Road | Gisborne | Lavenham 0902 | 2025-06-11 16:12 | 45819.675 | 2025-06-11 19:26 | 45819.8097 | 0.0074145 | 3.8219e-05 | 1 | 194 | Unplanned | Lightning | Replaced fuses
210 |  | 3648-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-12 09:02 | 45820.3764 | 2025-06-12 15:10 | 45820.6319 | 0.28129 | 0.00076438 | 20 | 3682.8129 | Planned | Planned | Replace 11kV poles
211 |  | 3673-26 | Lake Rd, Cricklewood Rd, Raupanga | Wairoa | Frasertown 3103 | 2025-06-12 10:00 | 45820.4167 | 2025-06-12 11:19 | 45820.4715 | 0.15207 | 0.0019492 | 51 | 3979 | Planned | Planned | Replace x-arm @ pole W4824
212 |  | 6062A-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-12 22:48 | 45820.95 | 2025-06-12 23:16 | 45820.9694 | 0.0074909 | 0.00026753 | 7 | 196 | Unplanned | Wildlife | Replaced fuses
213 |  | 6063A-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-13 07:14 | 45821.3014 | 2025-06-13 09:12 | 45821.3833 | 0.031569 | 0.00026753 | 7 | 826 | Unplanned | Wildlife | Replaced fuses
214 |  | 3658-26 | Titirangi Road | Wairoa | Frasertown 3103 | 2025-06-13 08:34 | 45821.3569 | 2025-06-13 13:46 | 45821.5736 | 0.19079 | 0.0006115 | 16 | 2497.7611 | Planned | Planned | Replace 11kV poles
215 |  | 3655-26 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-06-13 09:03 | 45821.3771 | 2025-06-13 15:25 | 45821.6424 | 0.2044 | 0.00053507 | 14 | 2675.4308 | Planned | Planned | Drop line for tree cutting
216 |  | 3649-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-13 09:04 | 45821.3778 | 2025-06-13 12:44 | 45821.5306 | 0.16816 | 0.00076438 | 20 | 2202.5225 | Planned | Planned | Replace 11kV poles
217 |  | 1855-26 | Ormond Township, Matawai Rd, Bond Rd, Whitmore Rd, Ngakaroa Rd | Gisborne | Waimata 0903 | 2025-06-14 03:33 | 45822.1479 | 2025-06-14 16:40 | 45822.6944 | 3.5693 | 0.021517 | 563 | 93392 | Unplanned | Third Party Interference | Car V's pole E185
218 |  | 6064A-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-15 04:19 | 45823.1799 | 2025-06-15 07:19 | 45823.3049 | 0.048156 | 0.00026753 | 7 | 1260 | Unplanned | Wildlife | Replaced fuses
219 |  | 6065A-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-15 09:54 | 45823.4125 | 2025-06-15 11:46 | 45823.4903 | 0.029964 | 0.00026753 | 7 | 784 | Unplanned | Wildlife | Replaced fuses
220 |  | 6066A-26 | 319 Whatatutu Road | Gisborne | Whatatutu 1201 | 2025-06-15 10:39 | 45823.4437 | 2025-06-15 14:03 | 45823.5854 | 0.015593 | 7.6438e-05 | 2 | 408 | Unplanned | Unknown cause | Replaced fuses
221 |  | 6067A-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-15 15:20 | 45823.6389 | 2025-06-15 16:30 | 45823.6875 | 0.018727 | 0.00026753 | 7 | 490 | Unplanned | Wildlife | Replaced fuses
222 |  | 1857-26 | Kopuapounamu road | Gisborne | Awatere 0101 | 2025-06-16 07:38 | 45824.3181 | 2025-06-16 13:41 | 45824.5701 | 0.22198 | 0.0006115 | 16 | 5808 | Unplanned | Defective Equipment | Conductor rusted out at pin between J2148 and J2149
223 |  | 1852-26 | Waikura road / Te Kumi | Gisborne | Hicks Bay 0102 | 2025-06-16 08:24 | 45824.35 | 2025-06-16 12:10 | 45824.5069 | 0.025912 | 0.00011466 | 3 | 678 | Unplanned | Lightning | To replace HV cross arm at pole J4667
224 |  | 3641A-26 | Motu Road | Gisborne | Matawai 1204 | 2025-06-16 09:02 | 45824.3764 | 2025-06-16 15:27 | 45824.6438 | 0.70629 | 0.0018345 | 48 | 9256.9509 | Planned | Planned | Replace HV poles
225 |  | 3651-26 | Pilmer road | Gisborne | Bushmere 0805 | 2025-06-16 09:13 | 45824.384 | 2025-06-16 13:11 | 45824.5493 | 0.40023 | 0.0016816 | 44 | 5247.0988 | Planned | Planned | Upgrade TX C252
226 |  | 6068A-26 | 2072 Kanakania road | Gisborne | Kanakanaia 1202 | 2025-06-16 14:44 | 45824.6139 | 2025-06-16 16:00 | 45824.6667 | 0.020333 | 0.00026753 | 7 | 532 | Unplanned | Third Party Interference | Replaced fuses
227 |  | 6069A-26 | 168 Andrews Road | Gisborne | Dalton 0502 | 2025-06-16 15:56 | 45824.6639 | 2025-06-16 18:30 | 45824.7708 | 0.011771 | 7.6438e-05 | 2 | 308 | Unplanned | Adverse Weather | Replaced fuses
228 |  | 3659-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-17 09:02 | 45825.3764 | 2025-06-17 14:30 | 45825.6042 | 0.25072 | 0.00076438 | 20 | 3282.5225 | Planned | Planned | Replace 11kV poles
229 |  | 3642-26 | Phillips Road | Gisborne | Matawai 1204 | 2025-06-17 09:10 | 45825.3819 | 2025-06-17 14:25 | 45825.6007 | 0.060195 | 0.00019109 | 5 | 787.672 | Planned | Planned | Replace HV Poles
230 |  | 6070A-26 | Mangatuna Quarry | Gisborne | Toko Tie 0401 | 2025-06-17 11:54 | 45825.4958 | 2025-06-17 12:50 | 45825.5347 | 0.0085611 | 0.00015288 | 4 | 224 | Unplanned | Wildlife | Replace fuses - big pond down end of HV line. HV line feeds water pump etc
231 |  | 6071A-26 | 7078 Waiapu Road | Gisborne | Makarika 0204 | 2025-06-17 17:00 | 45825.7083 | 2025-06-18 20:07 | 45826.8382 | 0.062182 | 3.8219e-05 | 1 | 1627 | Unplanned | Vegetation | Multiple fuses blown. Attended 17th strong winds/rain/fog could not get blown HV glass fuse back in. Spoke to customer 18th had blown HV fuse @ H1842, glass fuse @ TX H202 & LV porcelain changed to new NZI lineguard. TX pole needs replacing and trees in LV cut
232 |  | 3643-26 | Motu Rd, Marumoko Road | Gisborne | Matawai 1204 | 2025-06-18 09:05 | 45826.3785 | 2025-06-18 15:55 | 45826.6632 | 0.078349 | 0.00019109 | 5 | 1025.1959 | Planned | Planned | Replace HV Poles
233 |  | 6072A-26 | 1180 Wharerata Road | Gisborne | Muriwai 0905 | 2025-06-18 12:25 | 45826.5174 | 2025-06-18 13:10 | 45826.5486 | 0.012039 | 0.00026753 | 7 | 315 | Unplanned | Wildlife | Replaced fuses
234 |  | 1859-26 | Fraser Hill Road | Gisborne | Matawai 1204 | 2025-06-19 09:05 | 45827.3785 | 2025-06-19 11:49 | 45827.4924 | 0.025072 | 0.00015288 | 4 | 656 | Unplanned | Defective Equipment | Replace broken HV pole F2657
235 |  | 3663-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-06-19 09:06 | 45827.3792 | 2025-06-19 12:00 | 45827.5 | 0.133 | 0.00076438 | 20 | 1742.5225 | Planned | Planned | Replace 11kV Poles
236 |  | 1858-26 | Porter Street | Gisborne | Wainui 0504 | 2025-06-19 10:33 | 45827.4396 | 2025-06-19 11:20 | 45827.4722 | 0.14011 | 0.0029811 | 78 | 3666 | Unplanned | Defective Equipment | Replace burnt out LV rack TX A250
237 |  | 6073A-26 | 187 Berry Street | Gisborne | Tiniroto 1003 | 2025-06-23 07:24 | 45831.3083 | 2025-06-23 11:00 | 45831.4583 | 0.11557 | 0.00053507 | 14 | 3024 | Unplanned | Unknown cause | Replaced fuses
238 |  | 3687-26 | Waiapu Road | Gisborne | Makarika 0204 | 2025-06-24 09:09 | 45832.3812 | 2025-06-24 14:19 | 45832.5965 | 0.011848 | 3.8219e-05 | 1 | 310 | Planned | Planned | Replace TX structure H202
239 |  | 3660-26 | Judd Road | Gisborne | Lavenham 0902 | 2025-06-24 09:10 | 45832.3819 | 2025-06-24 11:40 | 45832.4861 | 0.028664 | 0.00019109 | 5 | 375.0717 | Planned | Planned | Install HV fuses D1942
240 |  | 3666-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-06-24 09:31 | 45832.3965 | 2025-06-24 15:03 | 45832.6271 | 0.4441 | 0.0013377 | 35 | 5817.7718 | Planned | Planned | Replace 11kV poles
241 |  | 6074A-26 | 37 Bond Road | Gisborne | Waimata 0903 | 2025-06-24 17:38 | 45832.7347 | 2025-06-24 18:15 | 45832.7604 | 0.0056564 | 0.00015288 | 4 | 148 | Unplanned | Unknown cause | Blown HV fuse, 10a line isolation fuse, middle phase
242 |  | 6075A-26 | 230 Campbell Road | Gisborne | Lavenham 0902 | 2025-06-25 08:16 | 45833.3444 | 2025-06-25 12:30 | 45833.5208 | 0.077661 | 0.00030575 | 8 | 2032 | Unplanned | Unknown cause | Replaced fuses
243 |  | 6076A-26 | 1117 Riverside Road | Gisborne | Waimata 0903 | 2025-06-25 08:48 | 45833.3667 | 2025-06-25 12:00 | 45833.5 | 0.13942 | 0.00072616 | 19 | 3648 | Unplanned | Unknown cause | Replaced fuses
244 |  | 3656-26 | Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-06-25 09:02 | 45833.3764 | 2025-06-25 11:42 | 45833.4875 | 0.02446 | 0.00015288 | 4 | 236.0361 | Planned | Planned | Cut trees
245 |  | 3646-26 | Phillips Road | Gisborne | Matawai 1204 | 2025-06-25 09:08 | 45833.3806 | 2025-06-25 15:19 | 45833.6382 | 0.070896 | 0.00019109 | 5 | 927.6772 | Planned | Planned | Replace 11kV poles
246 |  | 6077A-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-25 17:27 | 45833.7271 | 2025-06-25 18:15 | 45833.7604 | 0.012842 | 0.00026753 | 7 | 336 | Unplanned | Unknown cause | Replaced fuses
247 |  | 1863-26 | Tolaga Bay Sub | Gisborne | Tolaga Bay Sub 04 | 2025-06-26 09:13 | 45834.384 | 2025-06-26 10:16 | 45834.4278 | 0 | 0 | 0 | 0 | Unplanned | Defective Equipment | Refill SF6 Gas on 50kV CB G18. No customers off, as generator used.
248 |  | 6078A-26 | Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-06-26 09:15 | 45834.3854 | 2025-06-26 11:00 | 45834.4583 | 0.056182 | 0.00053507 | 14 | 1470 | Unplanned | Defective Equipment | Shutdown required to fix midspan sprag
249 |  | 1868-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2025-06-27 18:32 | 45835.7722 | 2025-06-29 11:37 | 45837.484 | 0.15551 | 0.0025225 | 66 | 4069 | Unplanned | Vegetation | Tree burning in line D2687-D2686
250 |  | 6079A-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-06-27 23:54 | 45835.9958 | 2025-06-28 07:15 | 45836.3021 | 0.11798 | 0.00026753 | 7 | 3087 | Unplanned | Wildlife | Replaced fuses
251 |  | 1866-26 | Waihau Bay Road | Gisborne | Rototahi 0403 | 2025-06-28 08:33 | 45836.3562 | 2025-06-30 13:25 | 45838.559 | 0.66329 | 0.0015288 | 40 | 17355 | Unplanned | Defective Equipment | Conductor corrosion apparent
252 |  | 6080A-26 | 41 Te Hue Road | Gisborne | Awatere 0101 | 2025-06-28 09:02 | 45836.3764 | 2025-06-28 15:43 | 45836.6549 | 0.030652 | 7.6438e-05 | 2 | 802 | Unplanned | Adverse Weather | Replaced fuses
253 |  | 3668-26 | Ruapapa Road | Wairoa | Raupunga 3101 | 2025-06-30 09:06 | 45838.3792 | 2025-06-30 15:34 | 45838.6486 | 0.17795 | 0.00045863 | 12 | 2329.0677 | Planned | Planned | To Replace 11kV Poles
254 |  | 3675-26 | Waione Road | Gisborne | Awatere 0101 | 2025-07-01 09:00 | 45839.375 | 2025-07-01 13:53 | 45839.5785 | 0.40313 | 0.0013759 | 36 | 5281.4298 | Planned | Planned | Replace HV poles
255 |  | 3674-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-07-02 08:30 | 45840.3542 | 2025-07-02 13:30 | 45840.5625 | 0.37837 | 0.0012612 | 33 | 4956.8674 | Planned | Planned | To Replace 11kV Poles
256 |  | 3670-26 | Puhunga Road | Gisborne | Makarika 0204 | 2025-07-02 08:31 | 45840.3549 | 2025-07-02 16:11 | 45840.6743 | 0.26371 | 0.00057328 | 15 | 3451.9778 | Planned | Planned | To replace 11kV poles
257 |  | 1869A-26 | Papanui Road | Wairoa | Morere 3401 | 2025-07-02 10:20 | 45840.4306 | 2025-07-02 13:06 | 45840.5458 | 0.28848 | 0.0032104 | 84 | 7548 | Unplanned | Defective Equipment | Replaced TX W129
258 |  | 3676-26 | Whangara Road | Gisborne | Dalton 0502 | 2025-07-02 11:38 | 45840.4847 | 2025-07-02 14:57 | 45840.6229 | 0.030422 | 0.00015288 | 4 | 398.0608 | Planned | Planned | To replace LV pole A4455
259 |  | 6048-26 | 335 Takapau Road | Gisborne | Tauwhareparae 0404 | 2025-07-03 08:31 | 45841.3549 | 2025-07-03 09:48 | 45841.4083 | 0.023543 | 0.00030575 | 8 | 616 | Unplanned | Unknown cause | Replace fuses
260 |  | 3679-26 | Karewa Road | Gisborne | Makarika 0204 | 2025-07-03 08:37 | 45841.359 | 2025-07-03 12:15 | 45841.5104 | 0.041659 | 0.00019109 | 5 | 545.1577 | Planned | Planned | Replace 11kV Poles
261 |  | 1873-26 | Onepoto Road | Gisborne | Hicks Bay 0102 | 2025-07-03 15:21 | 45841.6396 | 2025-07-04 16:46 | 45842.6986 | 1.055 | 0.0019874 | 52 | 27604 | Unplanned | Defective Equipment | To replace faulty transformer J513
262 |  | 1872-26 | McDonald Road | Gisborne | JNL_A 1405 | 2025-07-03 17:10 | 45841.7153 | 2025-07-04 15:34 | 45842.6486 | 0.41567 | 0.0013377 | 35 | 10876 | Unplanned | Third Party Interference | Car V's Pole C3349
263 |  | 3680-26 | Puhunga Road | Gisborne | Makarika 0204 | 2025-07-04 08:32 | 45842.3556 | 2025-07-04 15:18 | 45842.6375 | 0.23275 | 0.00057328 | 15 | 3046.7457 | Planned | Planned | Replace 11kV poles
264 |  | 6049-26 | 41 Te Hue Road | Gisborne | Awatere 0101 | 2025-07-04 09:26 | 45842.3931 | 2025-07-04 12:25 | 45842.5174 | 0.013682 | 7.6438e-05 | 2 | 358 | Unplanned | Adverse Weather | Big wind in area. Multiple trees & sags out on line
265 |  | 1874-26 | Mahia East coast Road | Wairoa | Mahia 3301 | 2025-07-04 12:35 | 45842.5243 | 2025-07-04 14:16 | 45842.5944 | 0.12815 | 0.001567 | 41 | 3353 | Unplanned | Defective Equipment | Repair broken jumper HV pole W698, Replace blown HV fuse W698
266 |  | 6050-26 | 66 Poroporo Road | Gisborne | Tiki Tiki 0206 | 2025-07-04 15:26 | 45842.6431 | 2025-07-04 16:48 | 45842.7 | 0.037607 | 0.00045863 | 12 | 984 | Unplanned | Adverse Weather | Replace fuses
267 |  | 1875-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-04 18:29 | 45842.7701 | 2025-07-08 14:55 | 45846.6215 | 2.1751 | 0.001567 | 41 | 56912 | Unplanned | Adverse Environment | Heavy rain resulted in floodwaters washing out pole J736
268 |  | 1877-26 | Wairoa Township | Wairoa | Borough One 3204 | 2025-07-05 10:10 | 45843.4236 | 2025-07-05 11:52 | 45843.4944 | 1.7996 | 0.031378 | 821 | 47087 | Unplanned | Unknown cause | No fault found
269 |  | 6051-26 | 591 SH 2, Wairoa | Wairoa | Raupunga 3101 | 2025-07-07 08:45 | 45845.3646 | 2025-07-07 10:10 | 45845.4236 | 0.061724 | 0.00072616 | 19 | 1615 | Unplanned | Unknown cause | 2 BlownHV fuses, Patrolled line. Replaced fuses
270 |  | 6052-26 | 6176 Waiapu Road | Gisborne | Makarika 0204 | 2025-07-07 09:48 | 45845.4083 | 2025-07-07 12:10 | 45845.5069 | 0.0054271 | 3.8219e-05 | 1 | 142 | Unplanned | Unknown cause | Replace fuses
271 |  | 1880-26 | Makaretu Road | Gisborne | Matawai 1204 | 2025-07-07 15:29 | 45845.6451 | 2025-07-08 15:54 | 45846.6625 | 0.60654 | 0.00068794 | 18 | 15870 | Unplanned | Defective Equipment | Conductor broke close to binder @ pole F754. Pole F754 replaced.
272 |  | 3681-26 | Fraser Hill Road | Gisborne | Matawai 1204 | 2025-07-08 08:34 | 45846.3569 | 2025-07-08 14:14 | 45846.5931 | 0.22091 | 0.00064972 | 17 | 2891.9882 | Planned | Planned | Replace HV poles
273 |  | 1881-26 | Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-07-08 13:45 | 45846.5729 | 2025-07-08 17:14 | 45846.7181 | 0.0079878 | 3.8219e-05 | 1 | 209 | Unplanned | Third Party Interference | Tree cut down contacted HV O/Head
274 |  | 6053-26 | 108 Kiwi Road | Wairoa | Nuhaka 3203 | 2025-07-09 09:06 | 45847.3792 | 2025-07-09 11:00 | 45847.4583 | 0.013071 | 0.00011466 | 3 | 342 | Unplanned | Wildlife | Birds, replace fuses
275 |  | 3682-26 | Churchill Avenue | Wairoa | Borough Two 3205 | 2025-07-09 10:58 | 45847.4569 | 2025-07-09 12:05 | 45847.5035 | 0.079381 | 0.0011848 | 31 | 1010.8056 | Planned | Planned | Carry out Maintenance on TX W1086
276 |  | 6054-26 | Totangi Road | Gisborne | Ngatapa 1102 | 2025-07-09 17:31 | 45847.7299 | 2025-07-09 18:30 | 45847.7708 | 0.0022549 | 3.8219e-05 | 1 | 59 | Unplanned | Unknown cause | Replace fuses
277 |  | 3683-26 | Fraser Hill Road | Gisborne | Matawai 1204 | 2025-07-10 08:32 | 45848.3556 | 2025-07-10 14:47 | 45848.616 | 0.057328 | 0.00015288 | 4 | 750.1147 | Planned | Planned | To Replace 11kV Poles
278 |  | 3714A-26 | Matawai Rd / Te Wera Road | Gisborne | Matawai 1204 | 2025-07-10 09:00 | 45848.375 | 2025-07-10 09:05 | 45848.3785 | 0.0026753 | 0.00053507 | 14 | 70 | Planned | Planned | Replace urgent HV Pole F1995 (Pole base washed away)
279 |  | 3714-26 | Matawai Rd / Te Wera Road | Gisborne | Matawai 1204 | 2025-07-10 09:00 | 45848.375 | 2025-07-10 14:34 | 45848.6069 | 0.72761 | 0.0021785 | 57 | 19038 | Planned | Planned | Replace urgent HV Pole F1995 (Pole base washed away)
280 |  | 3714C-26 | Matawai Rd / Te Wera Road | Gisborne | Matawai 1204 | 2025-07-10 09:00 | 45848.375 | 2025-07-10 14:34 | 45848.6069 | 0.012765 | 3.8219e-05 | 1 | 334 | Planned | Planned | Replace urgent HV Pole F1995 (Pole base washed away)
281 |  | 3714B-26 | Matawai Rd / Te Wera Road | Gisborne | Matawai 1204 | 2025-07-10 14:30 | 45848.6042 | 2025-07-10 14:34 | 45848.6069 | 0.0021403 | 0.00053507 | 14 | 56 | Planned | Planned | Replace urgent HV Pole F1995 (Pole base washed away)
282 |  | 6055-26 | 111 Richardson Road | Gisborne | Tiniroto 1003 | 2025-07-10 17:48 | 45848.7417 | 2025-07-10 19:30 | 45848.8125 | 0.027288 | 0.00026753 | 7 | 714 | Unplanned | Unknown cause | Replace fuses
283 |  | 3684-26 | Fraser Hill Road | Gisborne | Matawai 1204 | 2025-07-11 08:32 | 45849.3556 | 2025-07-11 13:27 | 45849.5604 | 0.045098 | 0.00015288 | 4 | 590.1101 | Planned | Planned | To Replace 11kV Poles
284 |  | 3689-26 | Matokitoki Valley road | Gisborne | Whangara 0506 | 2025-07-11 09:02 | 45849.3764 | 2025-07-11 11:49 | 45849.4924 | 0.24892 | 0.0014905 | 39 | 3261.3539 | Planned | Planned | Install new TX B1987
285 |  | 6056-26 | 25 Andrews Road | Gisborne | Dalton 0502 | 2025-07-11 15:58 | 45849.6653 | 2025-07-11 17:00 | 45849.7083 | 0.049761 | 0.0008026 | 21 | 1302 | Unplanned | Wildlife | Replace fuses
286 |  | 3688-26 | Motu | Gisborne | Matawai 1204 | 2025-07-12 09:02 | 45850.3764 | 2025-07-12 14:38 | 45850.6097 | 0.6164 | 0.0018345 | 48 | 8078.7935 | Planned | Planned | Replace Poles
287 |  | 1883-26 | Poroporo Valley Road | Gisborne | Tiki Tiki 0206 | 2025-07-12 11:45 | 45850.4896 | 2025-07-14 14:17 | 45852.5951 | 0.20661 | 0.00091726 | 24 | 5406 | Unplanned | Adverse Environment | Pole J1005 washed into river
288 |  | 3691-26 | Wharekopae Road | Gisborne | Lavenham 0902 | 2025-07-15 09:03 | 45853.3771 | 2025-07-15 13:00 | 45853.5417 | 0.0090579 | 3.8219e-05 | 1 | 118.5057 | Planned | Planned | Replace LV poles
289 |  | 1885-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-07-15 12:13 | 45853.509 | 2025-07-15 16:54 | 45853.7042 | 0.94248 | 0.0054271 | 142 | 24660 | Unplanned | Vegetation | Tree through line between poles G1779 - G1781
290 |  | 1887-26 | Mata Road | Gisborne | Mata 0304 | 2025-07-16 08:20 | 45854.3472 | 2025-07-16 08:22 | 45854.3486 | 0.0025989 | 0.0012994 | 34 | 68 | Unplanned | Defective Equipment | Customers affecting during switching operations. Failed PG clamp @ pole H2798
291 |  | 3696-26 | Raupapa Road | Wairoa | Raupunga 3101 | 2025-07-16 09:01 | 45854.3757 | 2025-07-16 15:09 | 45854.6312 | 0.16878 | 0.00045863 | 12 | 2209.0127 | Planned | Planned | To replace 11kV poles
292 |  | 1888-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-07-17 11:28 | 45855.4778 | 2025-07-17 12:55 | 45855.5382 | 0.0133 | 0.00015288 | 4 | 348 | Unplanned | Adverse Environment | Re-strained guy wires pole J2437A - Attained correct height
293 |  | 1891-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-07-18 01:15 | 45856.0521 | 2025-07-18 13:37 | 45856.5674 | 0.74741 | 0.0060386 | 158 | 19556 | Unplanned | Adverse Environment | Replace Pole D3851
294 |  | 1892-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2025-07-18 09:12 | 45856.3833 | 2025-07-18 16:49 | 45856.7007 | 0.66409 | 0.0018345 | 48 | 17376 | Unplanned | Vegetation | Tree through the line and wire down at pole D2689
295 |  | 6057-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-07-19 05:19 | 45857.2215 | 2025-07-19 07:25 | 45857.309 | 0.033709 | 0.00026753 | 7 | 882 | Unplanned | Wildlife | Replace fuses
296 |  | 6058-26 | 1184 Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-07-19 18:23 | 45857.766 | 2025-07-19 20:34 | 45857.8569 | 0.010013 | 7.6438e-05 | 2 | 262 | Unplanned | Unknown cause | Replace fuses
297 |  | 6059-26 | 732 Kopuaroa Road, Waipiro Bay | Gisborne | Inland 0301 | 2025-07-22 06:17 | 45860.2618 | 2025-07-22 08:20 | 45860.3472 | 0.094019 | 0.00076438 | 20 | 2460 | Unplanned | Defective Equipment | Faulty Stainless Steel HV fuse carrier
298 |  | 3705-26 | Hinaki St - Iranui Road | Gisborne | Crawford 1504 | 2025-07-22 08:30 | 45860.3542 | 2025-07-22 15:44 | 45860.6556 | 1.5758 | 0.0036308 | 95 | 20689.849 | Planned | Planned | Replace SD3 RMU with SF6 RMU
299 |  | 3692-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-22 09:00 | 45860.375 | 2025-07-22 16:57 | 45860.7063 | 0.71084 | 0.0014905 | 39 | 8783.6714 | Planned | Planned | To replace 11kV poles
300 |  | 6060-26 | 4314 Ihungia Road | Gisborne | Mata 0304 | 2025-07-23 07:20 | 45861.3056 | 2025-07-23 10:41 | 45861.4451 | 0.030728 | 0.00015288 | 4 | 804 | Unplanned | Unknown cause | Replace fuses
301 |  | 1896-26 | Manutuke | Gisborne | Muriwai 0905 | 2025-07-23 12:52 | 45861.5361 | 2025-07-23 13:55 | 45861.5799 | 0.22633 | 0.0035926 | 94 | 5922 | Unplanned | Defective Equipment | To Repair damaged conductor at Pole C1293
302 |  | 6061-26 | 1462 Ruakaka Road | Gisborne | Tiniroto 1003 | 2025-07-23 18:05 | 45861.7535 | 2025-07-23 20:45 | 45861.8646 | 0.13453 | 0.00084082 | 22 | 3520 | Unplanned | Unknown cause | Replace fuses
303 |  | 1899-26 | Tutamoe Road | Gisborne | Tauwhareparae 0404 | 2025-07-24 05:55 | 45862.2465 | 2025-07-24 16:02 | 45862.6681 | 0.25519 | 0.00042041 | 11 | 6677 | Unplanned | Vegetation | Tree branch was on the line at Pole G2510
304 |  | 3693-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-24 09:00 | 45862.375 | 2025-07-24 16:44 | 45862.6972 | 0.691 | 0.0014905 | 39 | 8783.6714 | Planned | Planned | To Replace 11kV Poles
305 |  | 3729-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-07-24 09:13 | 45862.384 | 2025-07-24 13:53 | 45862.5785 | 0.010701 | 3.8219e-05 | 1 | 280 | Planned | Planned | Replace Transformer E78 structure
306 |  | 3694-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-25 09:00 | 45863.375 | 2025-07-25 12:53 | 45863.5368 | 0.34684 | 0.0014905 | 39 | 4545.3259 | Planned | Planned | Replace HV Poles
307 |  | 3700-26 | Waione Road | Gisborne | Awatere 0101 | 2025-07-29 08:34 | 45867.3569 | 2025-07-29 12:26 | 45867.5181 | 0.133 | 0.00057328 | 15 | 1741.6769 | Planned | Planned | Isolate to cut trees
308 |  | 3708-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-29 09:00 | 45867.375 | 2025-07-29 13:31 | 45867.5632 | 0.40363 | 0.0014905 | 39 | 5288.3259 | Planned | Planned | Replace HV Poles
309 |  | 1900-26 | Mangapapa Area, Gisborne SW | Gisborne | Haisman 0804 | 2025-07-29 20:51 | 45867.8688 | 2025-07-29 23:29 | 45867.9785 | 2.6364 | 0.037302 | 976 | 68982 | Unplanned | Vegetation | Tree in lines at pole B6301
310 |  | 6062-26 | 41 Te Hue Road | Gisborne | Awatere 0101 | 2025-07-30 10:19 | 45868.4299 | 2025-07-30 13:50 | 45868.5764 | 0.016128 | 7.6438e-05 | 2 | 422 | Unplanned | Adverse Weather | Line patrol before reinstating fuses
311 |  | 1901-26 | Waiapu Road / Paroa Road | Gisborne | Toko Tie 0401 | 2025-07-30 10:49 | 45868.4507 | 2025-07-30 11:43 | 45868.4882 | 0.13243 | 0.0032486 | 85 | 3465 | Unplanned | Vegetation | Branch on line @ Pole G690
312 |  | 6063-26 | 654 Goodwin Road | Gisborne | Whangara 0506 | 2025-07-30 14:21 | 45868.5979 | 2025-07-30 15:40 | 45868.6528 | 0.0090579 | 0.00011466 | 3 | 237 | Unplanned | Unknown cause | Replace fuses
313 |  | 6064-26 | 3141 Mahia East Coast Road | Wairoa | Mahia 3301 | 2025-07-30 15:46 | 45868.6569 | 2025-07-30 19:30 | 45868.8125 | 0.077049 | 0.00034397 | 9 | 2016 | Unplanned | Adverse Weather | Replace fuses
314 |  | 3702-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-07-31 09:00 | 45869.375 | 2025-07-31 15:21 | 45869.6396 | 0.46597 | 0.001223 | 32 | 6103.4555 | Planned | Planned | Isolation for tree clearing
315 |  | 3710-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-07-31 09:01 | 45869.3757 | 2025-07-31 15:24 | 45869.6417 | 0.57011 | 0.0014905 | 39 | 7467.5813 | Planned | Planned | Replace HV Poles
316 |  | 3719-26 | Bowling Green Road | Gisborne | Ruatoria 0201 | 2025-07-31 09:02 | 45869.3764 | 2025-07-31 12:53 | 45869.5368 | 0.51206 | 0.0022167 | 58 | 6718.2853 | Planned | Planned | Replace HV Poles
317 |  | 6065-26 | 764 Awamate Road, Wairoa | Wairoa | Frasertown 3103 | 2025-07-31 19:10 | 45869.7986 | 2025-07-31 20:45 | 45869.8646 | 0.018154 | 0.00019109 | 5 | 475 | Unplanned | Unknown cause | Replace fuses
318 |  | 1902-26 | Te Araroa Road | Gisborne | Te Araroa 0103 | 2025-08-01 06:58 | 45870.2903 | 2025-08-01 11:18 | 45870.4708 | 1.2579 | 0.0048538 | 127 | 32913 | Unplanned | Adverse Weather | To Repair broken 11kV conductor betwn Pole J2644-J2643
319 |  | 3703-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2025-08-01 09:03 | 45870.3771 | 2025-08-01 12:58 | 45870.5403 | 0.11676 | 0.00049685 | 13 | 1528.4689 | Planned | Planned | To cut trees
320 |  | 1903-26 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2025-08-01 11:27 | 45870.4771 | 2025-08-01 16:18 | 45870.6792 | 0.068832 | 0.00042041 | 11 | 1801 | Unplanned | Defective Equipment | To Repair broken 11kV conductor between Pole D3766 - D3767
321 |  | 6066-26 | 503 Lake Road | Gisborne | Lavenham 0902 | 2025-08-02 06:53 | 45871.2868 | 2025-08-02 09:20 | 45871.3889 | 0.033709 | 0.00022931 | 6 | 882 | Unplanned | Unknown cause | Replace Fuses
322 |  | 1904-26 | Wairoa Township | Wairoa | Brickworks 3201 | 2025-08-02 12:31 | 45871.5215 | 2025-08-02 15:52 | 45871.6611 | 2.1929 | 0.02511 | 657 | 57376 | Unplanned | Defective Equipment | Blown HV cable betwn Pole W3124 & Ring main switch W1249
323 |  | 6067-26 | 416 Waiomatatini Road | Gisborne | Ruatoria 0201 | 2025-08-03 07:33 | 45872.3146 | 2025-08-03 08:50 | 45872.3681 | 0.0412 | 0.00053507 | 14 | 1078 | Unplanned | Adverse Weather | Replace Fuses
324 |  | 6068-26 | 108 Kiwi Road | Wairoa | Nuhaka 3203 | 2025-08-03 09:38 | 45872.4014 | 2025-08-03 10:58 | 45872.4569 | 0.0091726 | 0.00011466 | 3 | 240 | Unplanned | Wildlife | Replace Fuses
325 |  | 6069-26 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2025-08-04 06:50 | 45873.2847 | 2025-08-04 09:30 | 45873.3958 | 0.085611 | 0.00053507 | 14 | 2240 | Unplanned | Unknown cause | Replace Fuses
326 |  | 6070-26 | 4876 Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-08-04 08:25 | 45873.3507 | 2025-08-04 10:00 | 45873.4167 | 0.0036308 | 3.8219e-05 | 1 | 95 | Unplanned | Unknown cause | Replace Fuses
327 |  | 3698-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-08-04 09:07 | 45873.3799 | 2025-08-04 15:00 | 45873.625 | 0.13491 | 0.00038219 | 10 | 3530 | Planned | Planned | Isolation for tree clearing
328 |  | 3713-26 | Abbott Street | Gisborne | Childers 0605 | 2025-08-05 08:41 | 45874.3618 | 2025-08-05 16:02 | 45874.6681 | 1.7866 | 0.0040512 | 106 | 23467.689 | Planned | Planned | Replace oil RMU with new SF6 Unit
329 |  | 3727-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-08-05 09:03 | 45874.3771 | 2025-08-05 12:29 | 45874.5201 | 0.60061 | 0.0029429 | 77 | 7873.9051 | Planned | Planned | To install new TX F311
330 |  | 3699-26 | Te Hue road | Gisborne | Awatere 0101 | 2025-08-05 09:04 | 45874.3778 | 2025-08-05 15:02 | 45874.6264 | 0.027365 | 7.6438e-05 | 2 | 358.0274 | Planned | Planned | Clearing trees
331 |  | 3697-26 | Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-08-06 09:04 | 45875.3778 | 2025-08-06 15:37 | 45875.6507 | 0.06008 | 0.00015288 | 4 | 786.1202 | Planned | Planned | Tree Cutting
332 |  | 3749-26 | Crarer St | Wairoa | Brickworks 3201 | 2025-08-06 13:14 | 45875.5514 | 2025-08-06 17:52 | 45875.7444 | 1.1687 | 0.0072234 | 189 | 30579 | Planned | Planned | To reinstate HV cable at Pole W3124
333 |  | 3749-26 | Crarer St | Wairoa | Brickworks 3201 | 2025-08-06 13:14 | 45875.5514 | 2025-08-06 17:52 | 45875.7444 | 0.29375 | 0.0012612 | 33 | 7686 | Unplanned | Human Error | To reinstate HV cable at pole W3124 - missed advertising
334 |  | 3749-26 | Crarer St | Wairoa | Borough Two 3205 | 2025-08-06 13:17 | 45875.5535 | 2025-08-06 17:48 | 45875.7417 | 0.010357 | 3.8219e-05 | 1 | 271 | Planned | Planned | To reinstate HV cable at Pole W3124
335 |  | 4615-26 | Kowhai St / Ngairo St | Gisborne | Childers 0605 | 2025-08-06 14:05 | 45875.5868 | 2025-08-06 14:13 | 45875.5924 | 0.025377 | 0.0031722 | 83 | 664 | Unplanned | Defective Equipment | No oil in sight-glass on Ring Main Switch B1897. Had to switch from B1061 to TX B147 affected. Unplanned SAIDI from planned work
336 |  | 3747-26 | Frasertown Rd / Kaimoana Road | Wairoa | Borough One 3204 | 2025-08-07 08:16 | 45876.3444 | 2025-08-07 15:04 | 45876.6278 | 0.17153 | 0.00042041 | 11 | 4488 | Planned | Planned | Cable termination maintenance CB maintenance W217 / W218
337 |  | 3720-26 | Mohaka Coach Road | Wairoa | Raupunga 3101 | 2025-08-07 09:00 | 45876.375 | 2025-08-07 12:48 | 45876.5333 | 0.49669 | 0.0021785 | 57 | 5141.1756 | Planned | Planned | To Replace 11kV pole W5552
338 |  | 1905-26 | Putere Road | Wairoa | Raupunga 3101 | 2025-08-07 09:14 | 45876.3847 | 2025-08-07 11:27 | 45876.4771 | 0.13801 | 0.0017581 | 46 | 3611 | Unplanned | Unknown cause | Recloser W826 tripped and locked out. Patrol line & could not establish any fault
339 |  | 3726-26 | Arero Road | Gisborne | Mata 0304 | 2025-08-07 11:21 | 45876.4729 | 2025-08-07 12:33 | 45876.5229 | 0.0055035 | 7.6438e-05 | 2 | 33.0046 | Planned | Planned | Replace 11kV Pole H624
340 |  | 3723-26 | Kaiaua road | Gisborne | Toko Tie 0401 | 2025-08-08 08:35 | 45877.3576 | 2025-08-08 16:29 | 45877.6868 | 0.28985 | 0.0006115 | 16 | 3794.3188 | Planned | Planned | Replace Poles
341 |  | 3730-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-08-08 09:04 | 45877.3778 | 2025-08-08 12:31 | 45877.5215 | 0.45095 | 0.0021785 | 57 | 5918.126 | Planned | Planned | Replace HV Poles
342 |  | 1906-26 | Kaiwatau Road | Wairoa | Mahia 3301 | 2025-08-09 15:25 | 45878.6424 | 2025-08-09 20:48 | 45878.8667 | 0.43207 | 0.0013377 | 35 | 11305 | Unplanned | Adverse Weather | High winds broke conductor at pole W9119/ See also SW 1907
343 |  | 1907-26 | Mahia | Wairoa | Mahia 3301 | 2025-08-09 16:19 | 45878.6799 | 2025-08-10 10:42 | 45879.4458 | 6.5961 | 0.065584 | 1716 | 172587 | Unplanned | Unknown cause | Fault not found, suspect trees in YMCA Rd. Also blew jumper off at W794 on 2nd closing 17:44
344 |  | 1908-26 | Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2025-08-10 08:05 | 45879.3368 | 2025-08-13 09:07 | 45882.3799 | 0.48045 | 0.00076438 | 20 | 12571 | Unplanned | Defective Equipment | HV Jumper broken @ top of HV fuses TX D442
345 |  | 6071-26 | 66 Poroporo Road | Gisborne | Tiki Tiki 0206 | 2025-08-10 11:27 | 45879.4771 | 2025-08-10 13:11 | 45879.5493 | 0.047697 | 0.00045863 | 12 | 1248 | Unplanned | Unknown cause | Replace Fuses
346 |  | 1909-26 | Whakapunaki | Wairoa | Ruakituri 2003 | 2025-08-10 15:01 | 45879.6257 | 2025-08-11 10:05 | 45880.4201 | 0.090541 | 0.00042041 | 11 | 2369 | Unplanned | Vegetation | Tangled HV Conductor btwn Pole W1140-W7576 caused by the trees. Faultman estimates tree was 10m from line. Brushed through line when it fell.
347 |  | 6072-26 | 447 Kirkpatrick Road | Gisborne | Waimata 0903 | 2025-08-10 19:37 | 45879.8174 | 2025-08-10 20:15 | 45879.8438 | 0.011619 | 0.00030575 | 8 | 304 | Unplanned | Unknown cause | Replace Fuses
348 |  | 6073-26 | 174 Opou Road | Gisborne | Muriwai 0905 | 2025-08-11 04:44 | 45880.1972 | 2025-08-11 06:45 | 45880.2812 | 0.050869 | 0.00042041 | 11 | 1331 | Unplanned | Wildlife | Replace Fuses
349 |  | 6074-26 | 75A Sponge Bay Road | Gisborne | Wainui 0504 | 2025-08-11 06:24 | 45880.2667 | 2025-08-11 07:50 | 45880.3264 | 0.023008 | 0.00026753 | 7 | 602 | Unplanned | Unknown cause | 2 or 3 blown HV fuses
350 |  | 6075-26 | 2238 Tiniroto Road | Wairoa | Ruakituri 2003 | 2025-08-11 07:58 | 45880.3319 | 2025-08-11 10:10 | 45880.4236 | 0.055494 | 0.00042041 | 11 | 1452 | Unplanned | Adverse Weather | Replace Fuses - Also replaced fuses at W1140
351 |  | 3724-26 | Kaiaua road | Gisborne | Toko Tie 0401 | 2025-08-11 08:38 | 45880.3597 | 2025-08-11 15:34 | 45880.6486 | 0.25439 | 0.0006115 | 16 | 3330.0351 | Planned | Planned | Replace HV Poles G779 - G781 - G783
352 |  | 6076-26 | 3960 SH2, Morere | Wairoa | Morere 3401 | 2025-08-11 11:52 | 45880.4944 | 2025-08-11 13:55 | 45880.5799 | 0.0047009 | 3.8219e-05 | 1 | 123 | Unplanned | Unknown cause | Replace Fuses
353 |  | 1910-26 | Mangaharei Street | Gisborne | Ruatoria 0201 | 2025-08-11 18:00 | 45880.75 | 2025-08-11 18:47 | 45880.7826 | 0.092758 | 0.0032104 | 84 | 2427 | Unplanned | Defective Equipment | Loose DDO fuse to TX J87 (Stainless Steel)
354 |  | 3725-26 | Kaiaua road | Gisborne | Toko Tie 0401 | 2025-08-12 08:34 | 45881.3569 | 2025-08-12 15:22 | 45881.6403 | 0.24949 | 0.0006115 | 16 | 3265.9959 | Planned | Planned | Pole Replacements
355 |  | 3731A-26 | Marumoko Road / Motu Falls Road | Gisborne | Matawai 1204 | 2025-08-12 09:02 | 45881.3764 | 2025-08-12 15:32 | 45881.6472 | 0.25339 | 0.00064972 | 17 | 3317.1538 | Planned | Planned | Replace HV Poles
356 |  | 6077-26 | 271 Kaiwaitau Road | Wairoa | Mahia 3301 | 2025-08-13 06:39 | 45882.2771 | 2025-08-13 08:06 | 45882.3375 | 0.11638 | 0.0013377 | 35 | 3045 | Unplanned | Unknown cause | Replace Fuses
357 |  | 3728-26 | Tuai | Wairoa | Village 2002 | 2025-08-13 09:00 | 45882.375 | 2025-08-13 18:02 | 45882.7514 | 3.5335 | 0.0066501 | 174 | 39255.8571 | Planned | Planned | Replace SW/GR
358 |  | 3716-26 | Utting Road | Gisborne | Waimata 0903 | 2025-08-13 09:08 | 45882.3806 | 2025-08-13 14:39 | 45882.6104 | 0.1265 | 0.00038219 | 10 | 3310 | Planned | Planned | To cut trees
359 |  | 1912-26 | Makaraka Sub | Gisborne | Makaraka LS 0820 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:22 | 45882.4736 | 0.00049685 | 3.8219e-05 | 1 | 13 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
360 |  | 1912-26 | Makaraka Sub | Gisborne | Campion 0802 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:22 | 45882.4736 | 0.3632 | 0.027938 | 731 | 9503 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
361 |  | 1912-26 | Makaraka Sub | Gisborne | Nelson 0803 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:22 | 45882.4736 | 0.45412 | 0.034932 | 914 | 11882 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
362 |  | 1912-26 | Makaraka Sub | Gisborne | Haisman 0804 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:22 | 45882.4736 | 0.48492 | 0.037302 | 976 | 12688 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
363 |  | 1912-26 | Makaraka Sub | Gisborne | Bushmere 0805 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:22 | 45882.4736 | 0.090923 | 0.0069941 | 183 | 2379 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
364 |  | 1912-26 | Parkinson Sub | Gisborne | Lytton 0701 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.04613 | 0.0027135 | 71 | 1207 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
365 |  | 1912-26 | Parkinson Sub | Gisborne | Willows 0702 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.053927 | 0.0031722 | 83 | 1411 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
366 |  | 1912-26 | Parkinson Sub | Gisborne | Elgin 0703 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.60814 | 0.035773 | 936 | 15912 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
367 |  | 1912-26 | Parkinson Sub | Gisborne | Cedenco A 0704 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.0019492 | 0.00011466 | 3 | 51 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
368 |  | 1912-26 | Parkinson Sub | Gisborne | Innes 0705 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.020141 | 0.0011848 | 31 | 527 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
369 |  | 1912-26 | Parkinson Sub | Gisborne | Solander 0706 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.027288 | 0.0016052 | 42 | 714 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
370 |  | 1912-26 | Parkinson Sub | Gisborne | Chalmers 0707 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:26 | 45882.4764 | 0.46325 | 0.02725 | 713 | 12121 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
371 |  | 1912-26 | JNL Sub | Gisborne | JNL LS 1620 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:27 | 45882.4771 | 0.00068794 | 3.8219e-05 | 1 | 18 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
372 |  | 1912-26 | JNL Sub | Gisborne | JNL B 1601 | 2025-08-13 11:09 | 45882.4646 | 2025-08-13 11:27 | 45882.4771 | 0.00068794 | 3.8219e-05 | 1 | 18 | Unplanned | Unknown cause | EF @ CB 182 (Massey-Makaraka 50kV). Line patrols unable to identify site or cause of fault. Restoration staggered
373 |  | 3751-26 | Hihiroroa Road | Gisborne | Ngatapa 1102 | 2025-08-15 09:02 | 45884.3764 | 2025-08-15 10:49 | 45884.4507 | 0.081789 | 0.00076438 | 20 | 1072.7518 | Planned | Planned | Isolate 11kV lines to cut trees
374 |  | 6078-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-08-15 13:33 | 45884.5646 | 2025-08-15 15:30 | 45884.6458 | 0.031301 | 0.00026753 | 7 | 819 | Unplanned | Unknown cause | Replace Fuses
375 |  | 1915-26 | Kaiaua Road | Gisborne | Toko Tie 0401 | 2025-08-16 18:46 | 45885.7819 | 2025-08-17 11:34 | 45886.4819 | 0.1291 | 0.0006115 | 16 | 3378 | Unplanned | Unknown cause | Unable to identify site of fault
376 |  | 6079-26 | 503 Lake Road | Gisborne | Lavenham 0902 | 2025-08-17 08:16 | 45886.3444 | 2025-08-17 09:40 | 45886.4028 | 0.019262 | 0.00022931 | 6 | 504 | Unplanned | Unknown cause | Replace Fuses
377 |  | 1916-26 | Whangara Road | Gisborne | Dalton 0502 | 2025-08-17 11:42 | 45886.4875 | 2025-08-17 13:23 | 45886.5576 | 0.29708 | 0.0034397 | 90 | 7773 | Unplanned | Third Party Interference | Car v's Pole A645 - Pole damaged. Pole safe until replacement booked. Insulator off spindle, pole A644. Repaired/Replaced insulator
378 |  | 1917-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-08-17 11:49 | 45886.4924 | 2025-08-18 14:03 | 45887.5854 | 0.14237 | 0.00072616 | 19 | 3725 | Unplanned | Vegetation | Tree through HV line Btwn Pole J2715 - J2718
379 |  | 3736-26 | Matawai Road | Gisborne | Te Karaka 1203 | 2025-08-19 08:33 | 45888.3562 | 2025-08-19 16:16 | 45888.6778 | 0.76973 | 0.0017581 | 46 | 10077.9493 | Planned | Planned | Connect HV cables to new line through Nesbitts Dip
380 |  | 3740-26 | Marumoko Road | Gisborne | Matawai 1204 | 2025-08-19 09:01 | 45888.3757 | 2025-08-19 15:27 | 45888.6438 | 0.05901 | 0.00015288 | 4 | 772.118 | Planned | Planned | Replace HV Poles
381 |  | 3733-26 | Phillips Road | Gisborne | Matawai 1204 | 2025-08-19 09:06 | 45888.3792 | 2025-08-19 16:13 | 45888.6757 | 0.081598 | 0.00019109 | 5 | 1067.704 | Planned | Planned | To Replace 11kV Poles
382 |  | 6080-26 | 158 Wahau Road | Gisborne | Rototahi 0403 | 2025-08-19 09:34 | 45888.3986 | 2025-08-19 15:29 | 45888.6451 | 0.040703 | 0.00011466 | 3 | 1065 | Unplanned | Unknown cause | Replace Fuses
383 |  | 6081-26 | 654 Goodwin Road | Gisborne | Whangara 0506 | 2025-08-19 18:57 | 45888.7896 | 2025-08-19 20:40 | 45888.8611 | 0.059048 | 0.00057328 | 15 | 1545 | Unplanned | Unknown cause | Replace Fuses
384 |  | 1919-26 | Tahaenui Mahia | Wairoa | Morere 3401 | 2025-08-19 20:57 | 45888.8729 | 2025-08-19 21:20 | 45888.8889 | 0.23294 | 0.010128 | 265 | 6095 | Unplanned | Adverse Weather | Suspected wind clash (Strong Southerlies) caused conductor clash on Tahaenui-Mahia 33kV. Indicated by Tahaenui LFI BC OC
385 |  | 1919-26 | Tahaenui Mahia | Wairoa | Mahia 3301 | 2025-08-19 20:57 | 45888.8729 | 2025-08-19 23:09 | 45888.9646 | 1.3176 | 0.064475 | 1687 | 34474 | Unplanned | Adverse Weather | Suspected wind clash (Strong Southerlies) caused conductor clash on Tahaenui-Mahia 33kV. Indicated by Tahaenui LFI BC OC
386 |  | 6082-26 | 75A Sponge Bay Road | Gisborne | Wainui 0504 | 2025-08-20 06:45 | 45889.2812 | 2025-08-20 07:45 | 45889.3229 | 0.016052 | 0.00026753 | 7 | 420 | Unplanned | Unknown cause | Replace Fuses
387 |  | 1920-26 | Gordon Road | Gisborne | Te Arai 0906 | 2025-08-20 10:36 | 45889.4417 | 2025-08-20 17:05 | 45889.7118 | 0.17841 | 0.00045863 | 12 | 4668 | Unplanned | Defective Equipment | HV conductor broken btwn Poles C2739-C2740. Steel conductor - rotten
388 |  | 1921-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2025-08-21 09:08 | 45890.3806 | 2025-08-21 14:11 | 45890.591 | 0.20845 | 0.00068794 | 18 | 5454 | Unplanned | Adverse Weather | HV Conductor wrap btwn poles D2686-D2687
389 |  | 3741-26 | Marumoko road | Gisborne | Matawai 1204 | 2025-08-21 09:09 | 45890.3812 | 2025-08-21 14:29 | 45890.6035 | 0.04892 | 0.00015288 | 4 | 640.0978 | Planned | Planned | To Replace 11kV Poles
390 |  | 6083-26 | 209 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-08-21 15:13 | 45890.634 | 2025-08-21 16:00 | 45890.6667 | 0.012574 | 0.00026753 | 7 | 329 | Unplanned | Unknown cause | Replace Fuses
391 |  | 1916-26 | Whangara Rd, Pa Rd, Waiomoko Rd, Glenroy Rd | Gisborne | Dalton 0502 | 2025-08-22 08:40 | 45891.3611 | 2025-08-22 12:51 | 45891.5354 | 0.78464 | 0.0034779 | 91 | 20530 | Planned | Planned | Replace HV Pole A645 - Damaged by Vehicle 17/8/25. Whangara school - generator connected
392 |  | 6084-26 | 56 Mohaka Township Road | Wairoa | Raupunga 3101 | 2025-08-24 22:18 | 45893.9292 | 2025-08-24 23:39 | 45893.9854 | 0.012383 | 0.00015288 | 4 | 324 | Unplanned | Unknown cause | Replace Fuses
393 |  | 1924-26 | Te Araroa / Hicks Bay | Gisborne | Te Araroa 0103 | 2025-08-25 14:52 | 45894.6194 | 2025-08-25 15:06 | 45894.6292 | 0.067953 | 0.0048538 | 127 | 1778 | Unplanned | Defective Equipment | Incomer CB J526 failed during restoration to network supply
394 |  | 1924-26 | Te Araroa / Hicks Bay | Gisborne | Hicks Bay 0102 | 2025-08-25 14:52 | 45894.6194 | 2025-08-25 15:25 | 45894.6424 | 0.31248 | 0.0098605 | 258 | 8176 | Unplanned | Defective Equipment | Incomer CB J526 failed during restoration to network supply
395 |  | 1922-26 | Carroll St / Ormond Road | Wairoa | Borough Two 3205 | 2025-08-25 17:29 | 45894.7285 | 2025-08-25 19:29 | 45894.8118 | 0.0091726 | 7.6438e-05 | 2 | 240 | Unplanned | Third Party Interference | HV deenergised to allow work team to connect new cable to LV O/head & liven distribution pillar at base of pole. Originated from LV planned work, but notice only given on the day to make 11kV line safe.
396 |  | 1923-26 | King Road | Gisborne | Bushmere 0805 | 2025-08-25 18:41 | 45894.7785 | 2025-08-27 15:55 | 45896.6632 | 0.95551 | 0.0092108 | 241 | 25001 | Unplanned | Third Party Interference | Car V's Pole C5576: Team to replace broken HV Pole C5576, Faulty TX C262 and also replace cracked TX Pole C348. Note, refer to switching 3753 for related planned outage.
397 |  | 6085-26 | 200 Campbell Road | Gisborne | Lavenham 0902 | 2025-08-26 07:42 | 45895.3208 | 2025-08-26 09:53 | 45895.4118 | 0.040054 | 0.00030575 | 8 | 1048 | Unplanned | Unknown cause | Replace fuses
398 |  | 3754-26 | Kaiwaitau Road | Wairoa | Mahia 3301 | 2025-08-26 08:33 | 45895.3562 | 2025-08-26 13:36 | 45895.5667 | 0.40531 | 0.0013377 | 35 | 5311.6296 | Planned | Planned | Replace HV Pole W9123
399 |  | 3758-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-08-26 09:03 | 45895.3771 | 2025-08-26 16:26 | 45895.6847 | 0.10159 | 0.00022931 | 6 | 1329.3048 | Planned | Planned | Replace 11kV Pole
400 |  | 3753-26 | King Rd / Tucker Lane / Pilmer Rd | Gisborne | Bushmere 0805 | 2025-08-26 09:04 | 45895.3778 | 2025-08-26 12:30 | 45895.5208 | 0.27556 | 0.0013377 | 35 | 3609.8223 | Planned | Planned | Shelterbelt trimming - Pilmer Rd. Note, related to switching 1923.
401 |  | 3748-26 | Waiapu Road | Gisborne | Inland 0301 | 2025-08-26 09:15 | 45895.3854 | 2025-08-26 11:27 | 45895.4771 | 0.015135 | 0.00011466 | 3 | 198.031 | Planned | Planned | Replace HV Pole H2034
402 |  | 6086-26 | 4934 Waiapu Road, Te Puia Springs | Gisborne | Inland 0301 | 2025-08-26 16:13 | 45895.6757 | 2025-08-26 17:20 | 45895.7222 | 0.0025607 | 3.8219e-05 | 1 | 67 | Unplanned | Unknown cause | Replace Fuses
403 |  | 3793-26 | Apatu Road | Wairoa | Brickworks 3201 | 2025-08-27 08:31 | 45896.3549 | 2025-08-27 16:36 | 45896.6917 | 0.48194 | 0.00099369 | 26 | 12610 | Planned | Planned | To Replace oil RMU to New SF6 unit W285, W286, & W287
404 |  | 1925-26 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-08-28 07:49 | 45897.3257 | 2025-08-29 13:44 | 45898.5722 | 0.10426 | 0.00030575 | 8 | 2728 | Unplanned | Adverse Weather | High winds in area across this period, suspect clashing caused outages.
405 |  | 3756-26 | Lake Road | Wairoa | Frasertown 3103 | 2025-08-28 09:00 | 45897.375 | 2025-08-28 16:56 | 45897.7056 | 2.4524 | 0.005236 | 137 | 30545.3458 | Planned | Planned | Replace 11kV pole W1179
406 |  | 3759-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-08-28 09:02 | 45897.3764 | 2025-08-28 15:41 | 45897.6535 | 0.091496 | 0.00022931 | 6 | 1197.2745 | Planned | Planned | To Replace 11kV Poles
407 |  | 6087-26 | 75A Sponge Bay Road | Gisborne | Wainui 0504 | 2025-08-28 14:58 | 45897.6236 | 2025-08-28 16:45 | 45897.6979 | 0.028626 | 0.00026753 | 7 | 749 | Unplanned | Wildlife | Replace fuses
408 |  | 1926-26 | Armstrong Rd | Gisborne | Whatatutu 1201 | 2025-08-29 00:20 | 45898.0139 | 2025-08-29 13:26 | 45898.5597 | 1.1494 | 0.0076056 | 199 | 30074 | Unplanned | Vegetation | Tree through line @ Pole D1581 -confirmed out of zone by faultman
409 |  | 3760-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-08-29 09:02 | 45898.3764 | 2025-08-29 13:13 | 45898.5507 | 0.057558 | 0.00022931 | 6 | 753.227 | Planned | Planned | Replace Hv pole E1138
410 |  | 3762-26 | Awamate Road | Wairoa | Raupunga 3101 | 2025-08-29 10:01 | 45898.4174 | 2025-08-29 11:58 | 45898.4986 | 0.10285 | 0.00087904 | 23 | 1346.6827 | Planned | Planned | To Replace 11kV Pole W6104
411 |  | 6088-26 | 775 Panikau Road | Gisborne | Dalton 0502 | 2025-08-29 14:35 | 45898.6076 | 2025-08-29 16:00 | 45898.6667 | 0.029238 | 0.00034397 | 9 | 765 | Unplanned | Defective Equipment | Line clash, line sprags multiple
412 |  | 1928-26 | Hiriroroa Road South | Gisborne | Totangi 1101 | 2025-08-29 22:50 | 45898.9514 | 2025-08-29 23:56 | 45898.9972 | 0.031875 | 0.00095547 | 25 | 834 | Unplanned | Unknown cause | Power restored without identifying fault site
413 |  | 1927-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2025-08-30 12:31 | 45899.5215 | 2025-08-30 14:34 | 45899.6069 | 0.023505 | 0.00019109 | 5 | 615 | Unplanned | Wildlife | Possum caught between double pin @ Pole D3747
414 |  | 6089-26 | 4314 Ihungia Road | Gisborne | Mata 0304 | 2025-08-31 07:00 | 45900.2917 | 2025-08-31 10:27 | 45900.4354 | 0.031645 | 0.00015288 | 4 | 828 | Unplanned | Unknown cause | Replace fuses - windy
415 |  | 3794-26 | Douglas Street | Gisborne | Dalton 0502 | 2025-09-02 08:32 | 45902.3556 | 2025-09-02 16:48 | 45902.7 | 6.8783 | 0.014332 | 375 | 179971 | Planned | Planned | Replace RMU with Automated RMU
416 |  | 3771-26 | Paparatu Road | Gisborne | Te Arai 0906 | 2025-09-02 09:49 | 45902.409 | 2025-09-02 12:12 | 45902.5083 | 0.08198 | 0.00057328 | 15 | 1073.7899 | Planned | Planned | Replace poles C106 - C895
417 |  | 1929-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-09-02 11:03 | 45902.4604 | 2025-09-02 12:52 | 45902.5361 | 0.096388 | 0.00099369 | 26 | 2522 | Unplanned | Adverse Weather | Broken HV jumper @ bushing on TX F265
418 |  | 3764-26 | Rohepotae Road | Wairoa | Raupunga 3101 | 2025-09-03 08:37 | 45903.359 | 2025-09-03 16:44 | 45903.6972 | 0.33503 | 0.00068794 | 18 | 4259.9286 | Planned | Planned | Replace TX structure W1740. Drop span W394 - W1740
419 |  | 6090-26 | 4934A Lake Road, Tuai | Wairoa | Village 2002 | 2025-09-03 10:36 | 45903.4417 | 2025-09-03 13:31 | 45903.5632 | 0.0066883 | 3.8219e-05 | 1 | 175 | Unplanned | Defective Equipment | Replace Fuse
420 |  | 3768-26 | Cross Road | Gisborne | Ruatoria 0201 | 2025-09-03 13:34 | 45903.5653 | 2025-09-03 14:47 | 45903.616 | 0.04185 | 0.00057328 | 15 | 1095 | Planned | Planned | To Replace LV poles
421 |  | 6091-26 | 230 Campbell Road | Gisborne | Lavenham 0902 | 2025-09-03 13:47 | 45903.5743 | 2025-09-03 14:45 | 45903.6146 | 0.017734 | 0.00030575 | 8 | 464 | Unplanned | Unknown cause | Replace Fuse
422 |  | 6092-26 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2025-09-04 06:05 | 45904.2535 | 2025-09-04 09:00 | 45904.375 | 0.033442 | 0.00019109 | 5 | 875 | Unplanned | Unknown cause | Replace Fuse
423 |  | 3769-26 | Waiomatatini Road | Gisborne | Ruatoria 0201 | 2025-09-04 09:03 | 45904.3771 | 2025-09-04 14:03 | 45904.5854 | 0.16052 | 0.00053507 | 14 | 2101.1236 | Planned | Planned | To replace 11kV poles
424 |  | 6093-26 | 86 Cooper Road | Gisborne | Lavenham 0902 | 2025-09-04 09:35 | 45904.3993 | 2025-09-04 10:20 | 45904.4306 | 0.0034397 | 7.6438e-05 | 2 | 90 | Unplanned | Unknown cause | Replace Fuse
425 |  | 1931-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-09-06 08:16 | 45906.3444 | 2025-09-06 13:09 | 45906.5479 | 0.29115 | 0.00099369 | 26 | 7618 | Unplanned | Defective Equipment | Cradle arm @ TX F265 failed
426 |  | 1933-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-09-06 09:21 | 45906.3896 | 2025-09-06 15:28 | 45906.6444 | 0.23684 | 0.0021403 | 56 | 6197 | Unplanned | Defective Equipment | Broken HV Jumper @ TX F256 - Line side
427 |  | 6094-26 | 49 Moutohora Road | Gisborne | Matawai 1204 | 2025-09-06 14:28 | 45906.6028 | 2025-09-06 16:30 | 45906.6875 | 0.0046627 | 3.8219e-05 | 1 | 122 | Unplanned | Adverse Weather | Replace Fuse
428 |  | 1932-26 | Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-09-06 15:00 | 45906.625 | 2025-09-06 15:58 | 45906.6653 | 0.47277 | 0.0085993 | 225 | 12370 | Unplanned | Defective Equipment | HV jumper broken @ Pole J533
429 |  | 6095-26 | 764 Awamate Road, Wairoa | Wairoa | Frasertown 3103 | 2025-09-07 10:00 | 45907.4167 | 2025-09-07 11:00 | 45907.4583 | 0.011466 | 0.00019109 | 5 | 300 | Unplanned | Unknown cause | Blown isolation fuse, maybe birds
430 |  | 1934-26 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-09-08 07:03 | 45908.2937 | 2025-09-08 17:02 | 45908.7097 | 0.085381 | 0.00022931 | 6 | 2234 | Unplanned | Defective Equipment | HV Fuses TX G232 replaced - Earth band removed. Possible cause of OC fault due to tracking
431 |  | 1935-26 | Moanui Road | Gisborne | Matawai 1204 | 2025-09-08 13:19 | 45908.5549 | 2025-09-09 16:23 | 45909.6826 | 0.80688 | 0.00049685 | 13 | 21112 | Unplanned | Defective Equipment | Pole F2518 broken, due to floating HV conductor causing fire & burning through Pole
432 |  | 3778-26 | Main Road Tikitiki | Gisborne | Awatere 0101 | 2025-09-09 09:01 | 45909.3757 | 2025-09-09 16:40 | 45909.6944 | 0.31577 | 0.00068794 | 18 | 3773.5942 | Planned | Planned | Replace HV Poles
433 |  | 3819-26 | Tarewa Road | Gisborne | Te Arai 0906 | 2025-09-09 09:02 | 45909.3764 | 2025-09-09 13:25 | 45909.559 | 0.06031 | 0.00022931 | 6 | 1578 | Planned | Planned | Replace Poles
434 |  | 1936-26 | Lavenham road | Gisborne | Lavenham 0902 | 2025-09-09 18:21 | 45909.7646 | 2025-09-10 15:21 | 45910.6396 | 0.81705 | 0.0082171 | 215 | 21378 | Unplanned | Third Party Interference | Car hit Pole
435 |  | 6096-26 | 396 Stafford Road | Gisborne | Tahunga 1004 | 2025-09-10 07:31 | 45910.3132 | 2025-09-10 08:55 | 45910.3715 | 0.022473 | 0.00026753 | 7 | 588 | Unplanned | Unknown cause | Replace Fuse
436 |  | 3782-26 | Rockhill Road | Gisborne | W O Kuri 1001 | 2025-09-10 08:38 | 45910.3597 | 2025-09-10 11:16 | 45910.4694 | 0.018116 | 0.00011466 | 3 | 237.0568 | Planned | Planned | Replace poles
437 |  | 6097-26 | 2072 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-09-10 14:15 | 45910.5938 | 2025-09-10 16:57 | 45910.7063 | 0.04334 | 0.00026753 | 7 | 1134 | Unplanned | Unknown cause | Replace Fuse
438 |  | 1937-26 | Kakariki Farm Road | Wairoa | Raupunga 3101 | 2025-09-10 14:36 | 45910.6083 | 2025-09-10 20:33 | 45910.8562 | 0.056526 | 0.00026753 | 7 | 1479 | Unplanned | Defective Equipment | Broken jumper @ TX
439 |  | 1938-26 | Willow Flat Road | Wairoa | Raupunga 3101 | 2025-09-10 21:23 | 45910.891 | 2025-09-16 17:10 | 45916.7153 | 0.72903 | 0.01009 | 264 | 19075 | Unplanned | Vegetation | In Zone plantation trees through lines - High Winds
440 |  | 1939-26 | Kiwi Road | Wairoa | Nuhaka 3203 | 2025-09-10 22:16 | 45910.9278 | 2025-09-11 15:38 | 45911.6514 | 2.5633 | 0.012077 | 316 | 67069 | Unplanned | Adverse Weather | Wind clash brought conductor down & W7710-W7711. Fault current blew HV jumper & W6830. CB W215 out of alignment.
441 |  | 1942-26 | Waiapu Rd, Umakuri Radio Site | Gisborne | Mata 0304 | 2025-09-10 23:05 | 45910.9618 | 2025-09-11 18:27 | 45911.7688 | 0.12253 | 0.00015288 | 4 | 3206 | Unplanned | Defective Equipment | Lines down btwn H2722 & H2724. Two red tagged poles need to be replaced
442 |  | 1940-26 | Mohaka Coast road | Wairoa | Raupunga 3101 | 2025-09-11 00:11 | 45911.0076 | 2025-09-11 15:40 | 45911.6528 | 1.2234 | 0.0016434 | 43 | 32009 | Unplanned | Vegetation | Trees through line W4036 - W4037 - High Winds
443 |  | 1941-26 | Ihungia Road | Gisborne | Mata 0304 | 2025-09-11 02:40 | 45911.1111 | 2025-09-11 13:11 | 45911.5493 | 0.099178 | 0.0006115 | 16 | 2595 | Unplanned | Vegetation | Out of zone plantation tree fell across lines, breaking conductor
444 |  | 3779-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-09-11 09:01 | 45911.3757 | 2025-09-11 15:01 | 45911.6257 | 0.24766 | 0.00068794 | 18 | 3242.2289 | Planned | Planned | Replace 11kV poles J2381 & J2382
445 |  | 1943-26 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-09-12 07:05 | 45912.2951 | 2025-09-15 16:16 | 45915.6778 | 0.58471 | 0.00049685 | 13 | 15299 | Unplanned | Defective Equipment | Cracked insulators (Lightning?) x2. Tracking on X-Arm
446 |  | 6098-26 | 4314 Ihungia Road | Gisborne | Mata 0304 | 2025-09-12 07:10 | 45912.2986 | 2025-09-12 17:28 | 45912.7278 | 0.094477 | 0.00015288 | 4 | 2472 | Unplanned | Unknown cause | Replace fuse
447 |  | 3790-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-09-16 09:02 | 45916.3764 | 2025-09-16 13:00 | 45916.5417 | 0.20011 | 0.00084082 | 22 | 2621.0522 | Planned | Planned | Replace poles
448 |  | 3826-26 | Rangikohua Road | Gisborne | Tauwhareparae 0404 | 2025-09-16 09:06 | 45916.3792 | 2025-09-16 14:52 | 45916.6194 | 0.026448 | 7.6438e-05 | 2 | 692 | Planned | Planned | Disconnect 11kV lines to TX G247
449 |  | 3801-26 | Lake Road | Gisborne | Lavenham 0902 | 2025-09-16 09:09 | 45916.3812 | 2025-09-16 14:04 | 45916.5861 | 0.067648 | 0.00022931 | 6 | 885.2064 | Planned | Planned | Install new 15kVA TX D2048
450 |  | 3787-26 | Wharerata Road | Gisborne | Muriwai 0905 | 2025-09-17 08:32 | 45917.3556 | 2025-09-17 14:51 | 45917.6188 | 0.11588 | 0.00030575 | 8 | 1516.4635 | Planned | Planned | Replace 11kV poles
451 |  | 3806-26 | Mata Road | Gisborne | Mata 0304 | 2025-09-17 09:00 | 45917.375 | 2025-09-17 13:36 | 45917.5667 | 0.33744 | 0.001223 | 32 | 4419.3729 | Planned | Planned | Replace pole H1081
452 |  | 1946-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-09-17 20:50 | 45917.8681 | 2025-09-18 18:40 | 45918.7778 | 0.83661 | 0.002102 | 55 | 21890 | Unplanned | Defective Equipment | Pole J674 down
453 |  | 6099-26 | 120 Mangaroa Road | Wairoa | Ruakituri 2003 | 2025-09-18 06:59 | 45918.291 | 2025-09-18 10:15 | 45918.4271 | 0.014982 | 7.6438e-05 | 2 | 392 | Unplanned | Unknown cause | Replace Fuse
454 |  | 3791-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-09-18 08:32 | 45918.3556 | 2025-09-18 10:41 | 45918.4451 | 0.0049303 | 3.8219e-05 | 1 | 64.5063 | Planned | Planned | Remainder of shutdown cancelled due to highwinds - Helicopter unable to fly
455 |  | 6100-26 | 12 Okari Road | Wairoa | Ruakituri 2003 | 2025-09-18 08:54 | 45918.3708 | 2025-09-18 10:51 | 45918.4521 | 0.12073 | 0.0010319 | 27 | 3159 | Unplanned | Adverse Weather | Clashing wires due to wind. Replace fuses
456 |  | 3824-26 | Back Ormond Road | Gisborne | Haisman 0804 | 2025-09-18 09:02 | 45918.3764 | 2025-09-18 18:09 | 45918.7562 | 3.0522 | 0.00558 | 146 | 79862 | Planned | Planned | Relocate 50kV poles for subdivision development
457 |  | 1956-26 | Christopher Road | Gisborne | Dalton 0502 | 2025-09-18 11:13 | 45918.4674 | 2025-09-19 10:29 | 45919.4368 | 0.053354 | 3.8219e-05 | 1 | 1396 | Unplanned | Defective Equipment | Wind caused broken binder
458 |  | 6101-26 | 272 Barron Road | Gisborne | Whatatutu 1201 | 2025-09-18 11:20 | 45918.4722 | 2025-09-18 13:40 | 45918.5694 | 0.13377 | 0.00095547 | 25 | 3500 | Unplanned | Adverse Weather | Line clash from wind
459 |  | 1957-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-09-18 13:22 | 45918.5569 | 2025-09-18 20:50 | 45918.8681 | 0.95884 | 0.0021403 | 56 | 25088 | Unplanned | Defective Equipment | Broken HV conductor btwn Poles F2136 - F253
460 |  | 6102-26 | 359 Ngamotu Road | Wairoa | Affco 3202 | 2025-09-18 14:31 | 45918.6049 | 2025-09-18 15:10 | 45918.6319 | 0.0074527 | 0.00019109 | 5 | 195 | Unplanned | Adverse Weather | Replace fuse
461 |  | 6103-26 | 109 Stevens Road | Gisborne | Dalton 0502 | 2025-09-18 14:36 | 45918.6083 | 2025-09-18 18:46 | 45918.7819 | 0.066883 | 0.00026753 | 7 | 1750 | Unplanned | Unknown cause | Replace fuse
462 |  | 3795-26 | Pakowhai Road | Gisborne | Muriwai 0905 | 2025-09-18 14:40 | 45918.6111 | 2025-09-18 15:42 | 45918.6542 | 0.037913 | 0.0006115 | 16 | 497.4676 | Planned | Planned | Install new 3ph 30kVA transformer at Pole C4735
463 |  | 1949-26 | Murphy Rd - Lloyd George Rd | Gisborne | Tamarau 0503 | 2025-09-18 14:47 | 45918.616 | 2025-09-18 16:59 | 45918.7076 | 0.80214 | 0.0060768 | 159 | 20988 | Unplanned | Vegetation | Trees through HV caused broken conductor
464 |  | 1955-26 | Waikura Road | Gisborne | Hicks Bay 0102 | 2025-09-18 15:15 | 45918.6354 | 2025-09-19 06:30 | 45919.2708 | 0.24479 | 0.00026753 | 7 | 6405 | Unplanned | Vegetation | Branch across line at pole J4666
465 |  | 1954-26 | Blucks Pit Road | Wairoa | Morere 3401 | 2025-09-18 15:24 | 45918.6417 | 2025-09-19 15:33 | 45919.6479 | 0.11076 | 7.6438e-05 | 2 | 2898 | Unplanned | Defective Equipment | High winds broke hardwood pole W122
466 |  | 1953-26 | Kiwi Road | Wairoa | Nuhaka 3203 | 2025-09-18 15:51 | 45918.6604 | 2025-09-18 20:50 | 45918.8681 | 0.68993 | 0.0076438 | 200 | 18052 | Unplanned | Adverse Weather | Conductor down btwn W1196-W7711
467 |  | 3802-26 | Toreohaua Road | Gisborne | Lavenham 0902 | 2025-09-19 08:34 | 45919.3569 | 2025-09-19 14:45 | 45919.6146 | 0.028358 | 7.6438e-05 | 2 | 371.0284 | Planned | Planned | Replace TX pole D497
468 |  | 1966-26 | Potaka School | Gisborne | Hicks Bay 0102 | 2025-09-19 09:45 | 45919.4062 | 2025-09-19 14:36 | 45919.6083 | 0.033365 | 0.00011466 | 3 | 873 | Unplanned | Vegetation | Trees removed from LV circuit - removed HV fuses for safety
469 |  | 6104-26 | 1128 Te Wera Road | Gisborne | Matawai 1204 | 2025-09-19 16:52 | 45919.7028 | 2025-09-19 19:30 | 45919.8125 | 0.0060386 | 3.8219e-05 | 1 | 158 | Unplanned | Defective Equipment | Middle DDO carrier not holding properly.3ph TX, 2ph service. Swapped out L2 to L3 as L2 was the faulty DDO side
470 |  | 6105-26 | 1534 Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-09-20 08:13 | 45920.3424 | 2025-09-20 09:30 | 45920.3958 | 0.0029429 | 3.8219e-05 | 1 | 77 | Unplanned | Vegetation | Appears that a branch from tall willows across road has blown onto TX structure
471 |  | 1950-26 | Mangaroa | Wairoa | Ruakituri 2003 | 2025-09-20 09:55 | 45920.4132 | 2025-09-20 14:00 | 45920.5833 | 0.4829 | 0.0040894 | 107 | 12635 | Unplanned | Defective Equipment | Broken pole at W3764 located on 18/9. No fault caused at the time. High wind broke pole which was deteriorated at ground level.
472 |  | 6106-26 | 967 Mangamaia Road | Gisborne | Whatatutu 1201 | 2025-09-20 12:05 | 45920.5035 | 2025-09-20 13:45 | 45920.5729 | 0.095547 | 0.00095547 | 25 | 2500 | Unplanned | Adverse Weather | Replace Fuses
473 |  | 1958-26 | Whatatutu, Mangatu, Armstrong Rd | Gisborne | Whatatutu 1201 | 2025-09-20 12:57 | 45920.5396 | 2025-09-22 16:26 | 45922.6847 | 0.96434 | 0.0047392 | 124 | 25232 | Unplanned | Wildlife | A bird made contact with the conductor, which caused a fire on pole E734, resulting in power outage
474 |  | 3803-26 | Lake Road, Patutahi | Gisborne | Lavenham 0902 | 2025-09-22 08:31 | 45922.3549 | 2025-09-22 14:37 | 45922.609 | 0.40566 | 0.0011084 | 29 | 4775.7874 | Planned | Planned | Replace TX pole D320
475 |  | 3796-26 | Paritu Road | Gisborne | Muriwai 0905 | 2025-09-22 08:35 | 45922.3576 | 2025-09-22 13:13 | 45922.5507 | 0.010625 | 3.8219e-05 | 1 | 278 | Planned | Planned | Replace pole C3113
476 |  | 1962-26 | 1341 Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-09-22 10:27 | 45922.4354 | 2025-09-22 15:35 | 45922.6493 | 0.20883 | 0.0017581 | 46 | 5464 | Unplanned | Vegetation | Tree brought down HV conductors between poles D1787 - D1789
477 |  | 3757A-26 | Frasertown Road | Wairoa | Frasertown 3103 | 2025-09-23 08:31 | 45923.3549 | 2025-09-23 12:19 | 45923.5132 | 3.4618 | 0.015593 | 408 | 45531.4456 | Planned | Planned | Replace HV Pole W4117
478 |  | 3804-26 | Humphreys Road | Gisborne | Lavenham 0902 | 2025-09-23 08:36 | 45923.3583 | 2025-09-23 15:43 | 45923.6549 | 0.11424 | 0.00026753 | 7 | 1494.8998 | Planned | Planned | Replace TX Pole D456, Private pole but Network transformer. Network initiated replacement.
479 |  | 3800-26 | SH 35 | Gisborne | Makarika 0204 | 2025-09-23 09:01 | 45923.3757 | 2025-09-23 12:37 | 45923.5257 | 0.55586 | 0.0025989 | 68 | 7281.4771 | Planned | Planned | Replace ABS H71 with HV links H71
480 |  | 3805-26 | Kirkpatrick Road | Gisborne | Waimata 0903 | 2025-09-24 08:37 | 45924.359 | 2025-09-24 12:50 | 45924.5347 | 0.087025 | 0.00034397 | 9 | 1138.8916 | Planned | Planned | Replace TX Pole D334
481 |  | 1963-26 | Ihungia Road | Gisborne | Mata 0304 | 2025-09-24 08:46 | 45924.3653 | 2025-09-24 11:37 | 45924.484 | 0.019606 | 0.00011466 | 3 | 513 | Unplanned | Third Party Interference | Broken 11kV conductor at Pole H4180 due to a vehicle coming in contact with the power line
482 |  | 3811-26 | Otoko | Gisborne | Matawai 1204 | 2025-09-24 09:02 | 45924.3764 | 2025-09-24 16:13 | 45924.6757 | 0.71687 | 0.0017581 | 46 | 18757 | Planned | Planned | Replace Poles
483 |  | 6107-26 | 1312 Waihi Road | Wairoa | Frasertown 3103 | 2025-09-24 13:05 | 45924.5451 | 2025-09-24 14:44 | 45924.6139 | 0.0037837 | 3.8219e-05 | 1 | 99 | Unplanned | Unknown cause | Replace Fuses
484 |  | 3807-26 | Humphreys Road | Gisborne | Lavenham 0902 | 2025-09-25 08:33 | 45925.3562 | 2025-09-25 13:00 | 45925.5417 | 0.071431 | 0.00026753 | 7 | 934.809 | Planned | Planned | Replace TX D381
485 |  | 3835-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2025-09-25 09:02 | 45925.3764 | 2025-09-25 11:40 | 45925.4861 | 0.08454 | 0.00053507 | 14 | 2212 | Planned | Planned | Replace defect poles
486 |  | 1964-26 | Tuai, Lake, Ruakituri | Wairoa | Village 2002 | 2025-09-25 10:44 | 45925.4472 | 2025-09-25 11:08 | 45925.4639 | 0.16052 | 0.0066883 | 175 | 4200 | Unplanned | Defective Equipment | Restoring Tuai Sub to Normal configuration (refer SW 4654) open 110kV CB302 - Loss of comms to site. Switching completed manually onsite - Comms Restored. System now normal configuration.
487 |  | 1964-26 | Tuai, Lake, Ruakituri | Wairoa | Lake 2001 | 2025-09-25 10:44 | 45925.4472 | 2025-09-25 11:08 | 45925.4639 | 0.0091726 | 0.00038219 | 10 | 240 | Unplanned | Defective Equipment | Restoring Tuai Sub to Normal configuration (refer SW 4654) open 110kV CB302 - Loss of comms to site. Switching completed manually onsite - Comms restored. System now normal configuration.
488 |  | 1964-26 | Tuai, Lake, Ruakituri | Wairoa | Ruakituri 2003 | 2025-09-25 10:44 | 45925.4472 | 2025-09-25 11:08 | 45925.4639 | 0.14768 | 0.0061533 | 161 | 3864 | Unplanned | Defective Equipment | Restoring Tuai Sub to Normal configuration (refer SW 4654) open 110kV CB302 - Loss of comms to site. Switching completed manually onsite - Comms restored. System now normal configuration.
489 |  | 1964-26 | Tuai, Lake, Ruakituri | Wairoa | Genesis 2004 | 2025-09-25 10:44 | 45925.4472 | 2025-09-25 11:08 | 45925.4639 | 0.00091726 | 3.8219e-05 | 1 | 24 | Unplanned | Defective Equipment | Restoring Tuai Sub to Normal configuration (refer SW 4654) open 110kV CB302 - Loss of comms to site. Switching completed manually onsite - Comms restored. System now normal configuration.
490 |  | 6108-26 | 4988 Main Road | Gisborne | Hicks Bay 0102 | 2025-09-26 07:00 | 45926.2917 | 2025-09-26 10:20 | 45926.4306 | 0.022931 | 0.00011466 | 3 | 600 | Unplanned | Unknown cause | Replace Fuses
491 |  | 3809-26 | Tangihanga Road | Gisborne | Lavenham 0902 | 2025-09-26 08:34 | 45926.3569 | 2025-09-26 13:03 | 45926.5437 | 0.092528 | 0.00034397 | 9 | 1211.0108 | Planned | Planned | To replace TX pole D521
492 |  | 3813-26 | Makaretu Road | Gisborne | Matawai 1204 | 2025-09-26 09:00 | 45926.375 | 2025-09-26 15:10 | 45926.6319 | 0.25454 | 0.00068794 | 18 | 6660 | Planned | Planned | Replace 11kV Poles
493 |  | 1967-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-09-26 12:25 | 45926.5174 | 2025-09-26 12:32 | 45926.5222 | 0.0093637 | 0.001567 | 41 | 245 | Unplanned | Unknown cause | Blown HV fuses E347 due to unknown fault
494 |  | 1965-26 | Te Karaka | Gisborne | Te Karaka 1203 | 2025-09-26 13:33 | 45926.5646 | 2025-09-26 14:10 | 45926.5903 | 0.12161 | 0.0032868 | 86 | 3182 | Unplanned | Wildlife | Shutdown required to remove dead possum from ABS pole F397. Possum didn't initially cause an outage.
495 |  | 1968-26 | Nuhaka - Opoutama Rd | Wairoa | Mahia 3301 | 2025-09-26 14:58 | 45926.6236 | 2025-09-26 15:30 | 45926.6458 | 0.003669 | 0.00011466 | 3 | 96 | Unplanned | Defective Equipment | Coach screw rusted out on arm braces at pole W8735. Cross arm swaying.
496 |  | 6109-26 | 2161 Te Araroa Road | Gisborne | Awatere 0101 | 2025-09-27 09:11 | 45927.3826 | 2025-09-27 11:31 | 45927.4799 | 0.0053507 | 3.8219e-05 | 1 | 140 | Unplanned | Unknown cause | Replace Fuses
497 |  | 3808-26 | Humphreys Road | Gisborne | Lavenham 0902 | 2025-09-29 08:36 | 45929.3583 | 2025-09-29 13:15 | 45929.5521 | 0.074642 | 0.00026753 | 7 | 976.809 | Planned | Planned | Replace TX x-arms D394
498 |  | 3810-26 | Tiniroto Rd - Pipiwhakao Rd | Gisborne | Lavenham 0902 | 2025-09-30 08:31 | 45930.3549 | 2025-09-30 13:12 | 45930.55 | 0.27923 | 0.00099369 | 26 | 3656.63 | Planned | Planned | Replace TX Pole D628
499 |  | 3817-26 | Te Araroa Rd - Harrison Rd | Gisborne | Tiki Tiki 0206 | 2025-09-30 09:00 | 45930.375 | 2025-09-30 17:23 | 45930.7243 | 0.92284 | 0.0039748 | 104 | 11504.2975 | Planned | Planned | HV Pole Replacement
500 |  | 3815-26 | Makaretu Road | Gisborne | Matawai 1204 | 2025-09-30 09:02 | 45930.3764 | 2025-09-30 11:48 | 45930.4917 | 0.050755 | 0.00030575 | 8 | 664.4036 | Planned | Planned | Replace HV Poles
501 |  | 6110-26 | 783 Glenroy Road | Gisborne | Dalton 0502 | 2025-09-30 11:37 | 45930.484 | 2025-09-30 12:45 | 45930.5312 | 0.028588 | 0.00042041 | 11 | 748 | Unplanned | Wildlife | Replace Fuses
502 |  | 6111-26 | 597 Waihau Road | Gisborne | Rototahi 0403 | 2025-10-01 07:51 | 45931.3271 | 2025-10-01 09:05 | 45931.3785 | 0.039595 | 0.00053507 | 14 | 1036 | Unplanned | Unknown cause | Replace fuses
503 |  | 6112-26 | 1185 Hereheretau Road | Wairoa | Nuhaka 3203 | 2025-10-01 15:16 | 45931.6361 | 2025-10-01 17:15 | 45931.7188 | 0.036384 | 0.00030575 | 8 | 952 | Unplanned | Third Party Interference | Tree cutters were cutting trees in area and clashed lines together
504 |  | 6113-26 | 9/4 Apatu Street | Wairoa | Borough One 3204 | 2025-10-01 18:50 | 45931.7847 | 2025-10-01 21:15 | 45931.8854 | 0.20504 | 0.0014141 | 37 | 5365 | Unplanned | Defective Equipment | Replace fuses
505 |  | 1969-26 | Waimata | Gisborne | Waimata 0903 | 2025-10-02 05:57 | 45932.2479 | 2025-10-02 12:04 | 45932.5028 | 0.37309 | 0.0030575 | 80 | 9762 | Unplanned | Defective Equipment | HV conductor down btwn Poles A1940 - A1941
506 |  | 6114-26 | 220 Waione Road | Gisborne | Te Araroa 0103 | 2025-10-02 07:59 | 45932.3326 | 2025-10-02 12:15 | 45932.5104 | 0.2446 | 0.00095547 | 25 | 6400 | Unplanned | Vegetation | Patrol line prior to reinstating centre. Blown 10A HV fuse links. Manuka burning below line poles J4434 - J4435
507 |  | 1970-26 | Wharekaka Road | Gisborne | Toko Tie 0401 | 2025-10-02 08:02 | 45932.3347 | 2025-10-02 09:31 | 45932.3965 | 0.18368 | 0.0032104 | 84 | 4806 | Unplanned | Third Party Interference | Digger came in contact with the 11kV line betwn Pole G4071 - G4072
508 |  | 3818A-26 | Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-10-02 09:00 | 45932.375 | 2025-10-02 12:16 | 45932.5111 | 0.38888 | 0.0019874 | 52 | 5097.0475 | Planned | Planned | To replace 11kV pole J817, J806, J815
509 |  | 3825-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2025-10-02 09:02 | 45932.3764 | 2025-10-02 14:26 | 45932.6014 | 0.12383 | 0.00038219 | 10 | 1620.6306 | Planned | Planned | Replace HV pole. Replace ABS D264 with HV links
510 |  | 3855-26 | Paritu Road | Gisborne | Muriwai 0905 | 2025-10-03 08:33 | 45933.3562 | 2025-10-03 14:22 | 45933.5986 | 0.066692 | 0.00019109 | 5 | 1745 | Planned | Planned | Replace 11kV Poles
511 |  | 3827-26 | Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-10-03 09:02 | 45933.3764 | 2025-10-03 13:40 | 45933.5694 | 0.031875 | 0.00011466 | 3 | 417.0568 | Planned | Planned | Replace Poles
512 |  | 6115-26 | 181 Oliver Road | Gisborne | Matawai 1204 | 2025-10-04 12:07 | 45934.5049 | 2025-10-04 13:50 | 45934.5764 | 0.015746 | 0.00015288 | 4 | 412 | Unplanned | Lightning | Replace fuses
513 |  | 6116-26 | 5066 Matawai Road | Gisborne | Matawai 1204 | 2025-10-04 12:15 | 45934.5104 | 2025-10-04 15:00 | 45934.625 | 0.012612 | 7.6438e-05 | 2 | 330 | Unplanned | Lightning | Multiple locations within the address 1. F458, 2. F713, 3. F458, 4. F460, 5. F93. Note - duplicated this line as there were two different fuses
514 |  | 6117-26 | 5066 Matawai Road | Gisborne | Matawai 1204 | 2025-10-04 12:15 | 45934.5104 | 2025-10-04 15:00 | 45934.625 | 0.0063061 | 3.8219e-05 | 1 | 165 | Unplanned | Lightning | Multiple locations within the address 1. F458, 2. F713, 3. F458, 4. F460, 5. F93. Note - duplicated this line as there were two different fuses
515 |  | 1972-26 | Matawai Road | Gisborne | Matawai 1204 | 2025-10-04 12:29 | 45934.5201 | 2025-10-06 12:52 | 45936.5361 | 0.11095 | 3.8219e-05 | 1 | 2903 | Unplanned | Lightning | Replace faulty transformer after lightning strike
516 |  | 6118-26 | 159 Kaimoe Road | Gisborne | Lavenham 0902 | 2025-10-04 12:37 | 45934.5257 | 2025-10-04 14:50 | 45934.6181 | 0.030499 | 0.00022931 | 6 | 798 | Unplanned | Lightning | Replace fuses
517 |  | 6123-26 | 159 Kaimoe Road | Gisborne | Lavenham 0902 | 2025-10-04 12:37 | 45934.5257 | 2025-10-04 15:20 | 45934.6389 | 0.0062297 | 3.8219e-05 | 1 | 163 | Unplanned | Lightning | No # caller found fuse out due to lightning, feeds GM TX
518 |  | 6119-26 | 5893 Matawai Road | Gisborne | Matawai 1204 | 2025-10-04 12:54 | 45934.5375 | 2025-10-04 15:50 | 45934.6597 | 0.013453 | 7.6438e-05 | 2 | 352 | Unplanned | Lightning | Replace fuses
519 |  | 6120-26 | 261 Tiniroto Road | Gisborne | Lavenham 0902 | 2025-10-04 13:05 | 45934.5451 | 2025-10-04 16:50 | 45934.7014 | 0.017199 | 7.6438e-05 | 2 | 450 | Unplanned | Lightning | Replace fuses
520 |  | 6126-26 | 1737A Ohuka Road | Wairoa | Ruakituri 2003 | 2025-10-04 13:06 | 45934.5458 | 2025-10-04 18:17 | 45934.7618 | 0.011886 | 3.8219e-05 | 1 | 311 | Unplanned | Lightning | Replace fuses
521 |  | 6121-26 | 355 Tiniroto Road | Gisborne | Lavenham 0902 | 2025-10-04 13:07 | 45934.5465 | 2025-10-04 18:50 | 45934.7847 | 0.039327 | 0.00011466 | 3 | 1029 | Unplanned | Lightning | Replace fuses
522 |  | 6122-26 | 95 Kaimoe road | Gisborne | Lavenham 0902 | 2025-10-04 13:31 | 45934.5632 | 2025-10-04 16:00 | 45934.6667 | 0.017084 | 0.00011466 | 3 | 447 | Unplanned | Lightning | Replace fuses
523 |  | 6124-26 | 1746 SH2, Whakaki | Wairoa | Nuhaka 3203 | 2025-10-04 15:49 | 45934.659 | 2025-10-04 16:56 | 45934.7056 | 0.012803 | 0.00019109 | 5 | 335 | Unplanned | Lightning | Replace fuses
524 |  | 1971-26 | Wharekopae Road | Gisborne | Lavenham 0902 | 2025-10-04 16:18 | 45934.6792 | 2025-10-05 10:58 | 45935.4569 | 0.085611 | 7.6438e-05 | 2 | 2240 | Unplanned | Lightning | Transformer failed due to lightning strike. Replaced.
525 |  | 6125-26 | 172 Koranga Valley Road | Gisborne | Matawai 1204 | 2025-10-04 17:20 | 45934.7222 | 2025-10-04 18:45 | 45934.7812 | 0.0097458 | 0.00011466 | 3 | 255 | Unplanned | Lightning | Replace fuses
526 |  | 6127-26 | 6 Shaw Road | Gisborne | Matawai 1204 | 2025-10-04 18:00 | 45934.75 | 2025-10-04 20:45 | 45934.8646 | 0.012612 | 7.6438e-05 | 2 | 330 | Unplanned | Lightning | Replace fuses
527 |  | 6128-26 | 401 Titirangi Road | Wairoa | Frasertown 3103 | 2025-10-04 20:45 | 45934.8646 | 2025-10-04 21:36 | 45934.9 | 0.0019492 | 3.8219e-05 | 1 | 51 | Unplanned | Lightning | Replace fuses
528 |  | 6129-26 | 2740 Ihungia Road | Gisborne | Mata 0304 | 2025-10-04 21:24 | 45934.8917 | 2025-10-05 07:40 | 45935.3194 | 0.47086 | 0.00076438 | 20 | 12320 | Unplanned | Adverse Weather | Replace fuses
529 |  | 6130-26 | 6307 Matawai Road | Gisborne | Matawai 1204 | 2025-10-05 09:04 | 45935.3778 | 2025-10-05 11:45 | 45935.4896 | 0.012307 | 7.6438e-05 | 2 | 322 | Unplanned | Lightning | Replace fuses
530 |  | 6131-26 | 5322 Matawai Road | Gisborne | Matawai 1204 | 2025-10-05 15:08 | 45935.6306 | 2025-10-05 16:30 | 45935.6875 | 0.0062679 | 7.6438e-05 | 2 | 164 | Unplanned | Lightning | Replace fuses
531 |  | 6132-26 | 501 Waihua Valley Road | Wairoa | Raupunga 3101 | 2025-10-06 06:57 | 45936.2896 | 2025-10-06 08:30 | 45936.3542 | 0.0035544 | 3.8219e-05 | 1 | 93 | Unplanned | Unknown cause | Replace fuses
532 |  | 1976-26 | Waingake Road | Gisborne | Te Arai 0906 | 2025-10-06 07:05 | 45936.2951 | 2025-10-06 15:51 | 45936.6604 | 0.092949 | 0.00019109 | 5 | 2432 | Unplanned | Lightning | Replace faulty TX C55 due to Lightning
533 |  | 3829-26 | Pa Road | Gisborne | Dalton 0502 | 2025-10-07 09:03 | 45937.3771 | 2025-10-07 15:36 | 45937.65 | 0.46562 | 0.0011848 | 31 | 6098.7171 | Planned | Planned | Replace 11kV poles
534 |  | 1977-26 | Ruakituri Road | Wairoa | Ruakituri 2003 | 2025-10-07 13:03 | 45937.5437 | 2025-10-07 15:48 | 45937.6583 | 0.21441 | 0.0012994 | 34 | 5610 | Unplanned | Adverse Weather | Line patrolled from W1141 to W9856 - No fault found. Still windy. Restored supply via W9859. Closed and holding. Checked mains @ Whakapunaki Radio OK
535 |  | 6133-26 | 26 Oliver Road | Gisborne | Matawai 1204 | 2025-10-07 18:30 | 45937.7708 | 2025-10-08 09:14 | 45938.3847 | 0.033786 | 3.8219e-05 | 1 | 884 | Unplanned | Lightning | Replace fuses
536 |  | 6134-26 | 53 Kokohu Road | Wairoa | Morere 3401 | 2025-10-07 20:34 | 45937.8569 | 2025-10-07 21:37 | 45937.9007 | 0.016855 | 0.00026753 | 7 | 441 | Unplanned | Unknown cause | Replace fuses
537 |  | 3832-26 | Motu Falls Road | Gisborne | Matawai 1204 | 2025-10-08 09:02 | 45938.3764 | 2025-10-08 14:02 | 45938.5847 | 0.19492 | 0.00064972 | 17 | 5100 | Planned | Planned | Replace HV Poles
538 |  | 3857-26 | Tokomaru Bay Radio | Gisborne | Mata 0304 | 2025-10-08 09:06 | 45938.3792 | 2025-10-08 14:55 | 45938.6215 | 0.040015 | 0.00011466 | 3 | 1047 | Planned | Planned | Replace defected poles
539 |  | 3831-26 | Wainui / Makarori | Gisborne | Dalton 0502 | 2025-10-08 09:09 | 45938.3812 | 2025-10-08 09:41 | 45938.4035 | 0.45251 | 0.014141 | 370 | 6003.7149 | Planned | Planned | Test New RMU A79, A96, A98
540 |  | 3833-26 | Motu Falls Road | Gisborne | Matawai 1204 | 2025-10-09 09:02 | 45939.3764 | 2025-10-09 13:50 | 45939.5764 | 0.18712 | 0.00064972 | 17 | 2449.6568 | Planned | Planned | Replace HV Poles
541 |  | 3836-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-10-10 09:01 | 45940.3757 | 2025-10-10 13:12 | 45940.55 | 0.038372 | 0.00015288 | 4 | 502.0767 | Planned | Planned | Replace TX J311 structure
542 |  | 3858-26 | Waiapu Road | Gisborne | Mata 0304 | 2025-10-10 09:01 | 45940.3757 | 2025-10-10 11:24 | 45940.475 | 0.016396 | 0.00011466 | 3 | 429 | Planned | Planned | Replace 11kV Poles
543 |  | 1978-26 | Matawai Road | Gisborne | Bushmere 0805 | 2025-10-11 12:30 | 45941.5208 | 2025-10-11 17:01 | 45941.709 | 0.64216 | 0.0023696 | 62 | 16802 | Unplanned | Third Party Interference | To replace broken pole D601 caused by Car V's Pole
544 |  | 1979-26 | Harris Feeder | Gisborne | Harris 1502 | 2025-10-11 17:32 | 45941.7306 | 2025-10-11 17:55 | 45941.7465 | 0.74718 | 0.032486 | 850 | 19550 | Unplanned | Third Party Interference | Childs tent blown into HV lines in Sheehan St
545 |  | 6135-26 | 57 Rakaukaka Road, Manutuke | Gisborne | Te Arai 0906 | 2025-10-12 11:00 | 45942.4583 | 2025-10-12 11:55 | 45942.4965 | 0.014714 | 0.00026753 | 7 | 385 | Unplanned | Unknown cause | Replace fuses
546 |  | 6136-26 | 4 Lottin Point Rd | Gisborne | Hicks Bay 0102 | 2025-10-13 07:02 | 45943.2931 | 2025-10-13 10:35 | 45943.441 | 0.0081406 | 3.8219e-05 | 1 | 213 | Unplanned | Lightning | Replace fuses
547 |  | 6137-26 | 1262 Riverside Rd | Gisborne | Waimata 0903 | 2025-10-13 14:38 | 45943.6097 | 2025-10-13 15:45 | 45943.6562 | 0.048653 | 0.00072616 | 19 | 1273 | Unplanned | Unknown cause | Replace fuses
548 |  | 3838-26 | Bailie Road | Gisborne | Waimata 0903 | 2025-10-14 08:31 | 45944.3549 | 2025-10-14 13:47 | 45944.5743 | 0.12077 | 0.00038219 | 10 | 1580.6306 | Planned | Planned | Replace 11kV poles A1946 & A1953
549 |  | 3837-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2025-10-14 09:00 | 45944.375 | 2025-10-14 12:23 | 45944.516 | 0.7486 | 0.0037072 | 97 | 9807.5816 | Planned | Planned | Replace Pole G1703. Remove redundant o/head to G133
550 |  | 1982-26 | Raupunga, Kotemaori, Putere | Wairoa | Raupunga 3101 | 2025-10-14 14:00 | 45944.5833 | 2025-10-14 14:28 | 45944.6028 | 0.091955 | 0.0060386 | 158 | 2406 | Unplanned | Unknown cause | Earth fault at C phase indicated at W826
551 |  | 6138-26 | 388 Aberdeen Rd | Gisborne | Aberdeen 0609 | 2025-10-14 23:02 | 45944.9597 | 2025-10-15 00:10 | 45945.0069 | 0.21571 | 0.0031722 | 83 | 5644 | Unplanned | Unknown cause | Replace fuses
552 |  | 3834-26 | Ngakaroa Road | Gisborne | Waimata 0903 | 2025-10-15 08:35 | 45945.3576 | 2025-10-15 15:58 | 45945.6653 | 0.016931 | 3.8219e-05 | 1 | 221.5085 | Planned | Planned | Repace & Relocate HV Pole E2921
553 |  | 6139-26 | 84 Cooper Rd | Gisborne | Lavenham 0902 | 2025-10-15 09:44 | 45945.4056 | 2025-10-15 10:24 | 45945.4333 | 0.0030575 | 7.6438e-05 | 2 | 80 | Unplanned | Unknown cause | Replace fuses
554 |  | 6140-26 | 1180 Arakihi Rd | Gisborne | Tauwhareparae 0404 | 2025-10-15 12:42 | 45945.5292 | 2025-10-15 17:36 | 45945.7333 | 0.10113 | 0.00034397 | 9 | 2646 | Unplanned | Unknown cause | Replace fuses
555 |  | 3840-26 | Morere Road SH2 | Wairoa | Morere 3401 | 2025-10-16 08:30 | 45946.3542 | 2025-10-16 13:09 | 45946.5479 | 0.8957 | 0.0032104 | 84 | 11762.8587 | Planned | Planned | Replace HV poles W8348 & W8377
556 |  | 3839-26 | Bailie Road | Gisborne | Waimata 0903 | 2025-10-16 08:46 | 45946.3653 | 2025-10-16 14:11 | 45946.591 | 0.024842 | 7.6438e-05 | 2 | 325.0254 | Planned | Planned | Replace Pole A1948
557 |  | 3843-26 | Paparatu Road | Gisborne | Te Arai 0906 | 2025-10-17 09:01 | 45947.3757 | 2025-10-17 12:07 | 45947.5049 | 0.10663 | 0.00057328 | 15 | 1396.3004 | Planned | Planned | Replace HV poles C106 & C895
558 |  | 3845-26 | Lavenham Road | Gisborne | Lavenham 0902 | 2025-10-17 09:05 | 45947.3785 | 2025-10-17 11:04 | 45947.4611 | 0.28653 | 0.0024078 | 63 | 3771.4391 | Planned | Planned | Replace 11kV Pole D1694
559 |  | 3904-26 | 402 Aberdeen Road | Gisborne | Aberdeen 0609 | 2025-10-19 09:02 | 45949.3764 | 2025-10-19 11:24 | 45949.475 | 0.44502 | 0.003134 | 82 | 11644 | Planned | Planned | Replace HV Cable Lightning arrestors
560 |  | 6141-26 | 202 Maraehara Rd | Gisborne | Tiki Tiki 0206 | 2025-10-19 09:35 | 45949.3993 | 2025-10-19 11:35 | 45949.4826 | 0.0091726 | 7.6438e-05 | 2 | 240 | Unplanned | Wildlife | Replace fuses
561 |  | 1983-26 | Cooper Rd / Tansley Rd | Gisborne | Lavenham 0902 | 2025-10-20 14:02 | 45950.5847 | 2025-10-20 16:05 | 45950.6701 | 0.047009 | 0.00038219 | 10 | 1230 | Unplanned | Defective Equipment | Replace faulty transformer D739
562 |  | 6142-26 | 2740 Ihungia Road, Raukumara | Gisborne | Mata 0304 | 2025-10-20 16:01 | 45950.6674 | 2025-10-20 19:23 | 45950.8076 | 0.1544 | 0.00076438 | 20 | 4040 | Unplanned | Unknown cause | Replace fuses
563 |  | 6143-26 | 4314 Ihungia Road, Tokomaru Bay | Gisborne | Mata 0304 | 2025-10-21 06:08 | 45951.2556 | 2025-10-21 08:24 | 45951.35 | 0.10396 | 0.00076438 | 20 | 2720 | Unplanned | Unknown cause | Possibly be clashing due to high winds
564 |  | 6147-26 | 221 Shaw Rd | Gisborne | Matawai 1204 | 2025-10-21 07:53 | 45951.3285 | 2025-10-21 10:25 | 45951.434 | 0.052284 | 0.00034397 | 9 | 1368 | Unplanned | Unknown cause | Replace fuses
565 |  | 3841-26 | Te Wera Rd / Matawai | Gisborne | Matawai 1204 | 2025-10-21 08:31 | 45951.3549 | 2025-10-21 15:39 | 45951.6521 | 0.91603 | 0.0021403 | 56 | 12009.8579 | Planned | Planned | Replace 11kV Poles
566 |  | 3847-26 | Kaiaua road | Gisborne | Toko Tie 0401 | 2025-10-21 08:35 | 45951.3576 | 2025-10-21 15:44 | 45951.6556 | 0.26234 | 0.0006115 | 16 | 3434.0987 | Planned | Planned | Replace 11kV poles
567 |  | 3846-26 | Waikura road | Gisborne | Hicks Bay 0102 | 2025-10-21 09:02 | 45951.3764 | 2025-10-21 15:34 | 45951.6486 | 0.91959 | 0.0023696 | 62 | 12045.0554 | Planned | Planned | Install new ABS J129, new Recloser J650
568 |  | 3856-26 | Lucknow Street | Wairoa | Borough Two 3205 | 2025-10-21 09:04 | 45951.3778 | 2025-10-21 17:06 | 45951.7125 | 0.62633 | 0.0012994 | 34 | 7591.9327 | Planned | Planned | Replace TX W1539
569 |  | 6144-26 | 682 Titirangi Rd, Wairoa | Wairoa | Frasertown 3103 | 2025-10-21 12:20 | 45951.5139 | 2025-10-21 14:15 | 45951.5938 | 0.0087904 | 7.6438e-05 | 2 | 230 | Unplanned | Unknown cause | Replace fuses
570 |  | 6145-26 | 2280 Ruapapa Rd, Tuai | Wairoa | Raupunga 3101 | 2025-10-21 18:30 | 45951.7708 | 2025-10-21 20:29 | 45951.8535 | 0.050029 | 0.00042041 | 11 | 1309 | Unplanned | Adverse Weather | Replace fuses
571 |  | 6146-26 | 1283 Cricklewood Road , Raupunga | Wairoa | Raupunga 3101 | 2025-10-21 19:07 | 45951.7965 | 2025-10-22 08:30 | 45952.3542 | 0.12276 | 0.00015288 | 4 | 3212 | Unplanned | Adverse Weather | Replace fuses
572 |  | 6148-26 | 53 Kokohu Rd , Nuhaka | Wairoa | Morere 3401 | 2025-10-21 20:35 | 45951.8576 | 2025-10-21 22:30 | 45951.9375 | 0.030766 | 0.00026753 | 7 | 805 | Unplanned | Adverse Weather | Replace fuses
573 |  | 6149-26 | 770 Tutamoe Rd, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2025-10-22 06:12 | 45952.2583 | 2025-10-22 10:46 | 45952.4486 | 0.11519 | 0.00042041 | 11 | 3014 | Unplanned | Unknown cause | Replace fuses
574 |  | 6150-26 | 1 Kaitawa Rd , Tuai | Wairoa | Village 2002 | 2025-10-22 07:38 | 45952.3181 | 2025-10-22 11:30 | 45952.4792 | 0.48767 | 0.002102 | 55 | 12760 | Unplanned | Adverse Weather | Replace fuses
575 |  | 3887-26 | Waimaha | Gisborne | Tahora 1103 | 2025-10-22 09:04 | 45952.3778 | 2025-10-22 15:04 | 45952.6278 | 0.20638 | 0.00057328 | 15 | 2701.5479 | Planned | Planned | Replace 11kV TX Pole D480
576 |  | 6151-26 | 1706 A Parikanapa Rd | Gisborne | Parikanapa 1002 | 2025-10-22 12:40 | 45952.5278 | 2025-10-22 15:45 | 45952.6562 | 0.014141 | 7.6438e-05 | 2 | 370 | Unplanned | Unknown cause | Replace fuses
577 |  | 1987-26 | Waimata Road | Gisborne | Tahora 1103 | 2025-10-22 14:29 | 45952.6035 | 2025-10-22 15:08 | 45952.6306 | 0.0044716 | 0.00011466 | 3 | 117 | Unplanned | Defective Equipment | ABS D1306 - insulator broken. ABS closed and jumpered for replacement.
578 |  | 6152-26 | 488 Kaiaua Road, Tolaga Bay | Gisborne | Toko Tie 0401 | 2025-10-22 15:05 | 45952.6285 | 2025-10-22 18:10 | 45952.7569 | 0.0070705 | 3.8219e-05 | 1 | 185 | Unplanned | Defective Equipment | Replace all 3 DDO units stainless steel tops burning power not restored
579 |  | 6153-26 | 133 Moutohora Road, Motu | Gisborne | Matawai 1204 | 2025-10-22 19:18 | 45952.8042 | 2025-10-22 21:43 | 45952.9049 | 0.0055418 | 3.8219e-05 | 1 | 145 | Unplanned | Unknown cause | Replace fuses
580 |  | 1988-26 | Makaretu Road | Gisborne | Matawai 1204 | 2025-10-23 05:57 | 45953.2479 | 2025-10-23 13:30 | 45953.5625 | 0.37466 | 0.0017199 | 45 | 9803 | Unplanned | Defective Equipment | Broken conductor between pole F761 - F762
581 |  | 3907-26 | Munro Street | Gisborne | Elgin 0703 | 2025-10-23 08:31 | 45953.3549 | 2025-10-23 18:46 | 45953.7819 | 1.5748 | 0.0025607 | 67 | 41205 | Planned | Planned | Replace Ring Main Unit B706, B705, B704, B703
582 |  | 3890-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-10-23 08:32 | 45953.3556 | 2025-10-23 15:37 | 45953.6507 | 0.8284 | 0.0019492 | 51 | 10858.6241 | Planned | Planned | Replace 11kV poles
583 |  | 3848-26 | Kaiaua road | Gisborne | Toko Tie 0401 | 2025-10-23 08:34 | 45953.3569 | 2025-10-23 13:59 | 45953.5826 | 0.19874 | 0.0006115 | 16 | 2601.9234 | Planned | Planned | Replace 11kV pole G764
584 |  | 3849-26 | Lottin Point - Waikura | Gisborne | Hicks Bay 0102 | 2025-10-23 09:02 | 45953.3764 | 2025-10-23 14:40 | 45953.6111 | 0.6957 | 0.002102 | 55 | 9108.9397 | Planned | Planned | Replace ABS J368 with Recloser J4558. Note refer 3850 for additional 7 customers from J394 to EOL
585 |  | 3850-26 | Waikura Valley | Gisborne | Hicks Bay 0102 | 2025-10-23 09:02 | 45953.3764 | 2025-10-23 14:30 | 45953.6042 | 0.087751 | 0.00026753 | 7 | 1148.3071 | Planned | Planned | Install new TX J4656. Note this outage accompanies 3849
586 |  | 6154-26 | 7 Kaitawa Rd, Tuai | Wairoa | Village 2002 | 2025-10-23 09:59 | 45953.416 | 2025-10-23 12:00 | 45953.5 | 0.25435 | 0.002102 | 55 | 6655 | Unplanned | Adverse Weather | Replace fuses
587 |  | 6155-26 | 2740 Ihungia Road, Raukumara | Gisborne | Mata 0304 | 2025-10-23 12:13 | 45953.509 | 2025-10-23 18:02 | 45953.7514 | 0.26677 | 0.00076438 | 20 | 6980 | Unplanned | Adverse Weather | Replace fuses
588 |  | 6158-26 | 104 Aranui Rd, Frasertown | Wairoa | Raupunga 3101 | 2025-10-23 12:18 | 45953.5125 | 2025-10-23 15:15 | 45953.6354 | 0.10824 | 0.0006115 | 16 | 2832 | Unplanned | Adverse Weather | Replace fuses
589 |  | 6156-26 | 73 Brownlie Rd, Frasertown | Wairoa | Frasertown 3103 | 2025-10-23 13:01 | 45953.5424 | 2025-10-23 14:06 | 45953.5875 | 0.0074527 | 0.00011466 | 3 | 195 | Unplanned | Vegetation | Replace fuses
590 |  | 6157-26 | 303 Ngamotu Rd, Wairoa | Wairoa | Affco 3202 | 2025-10-23 13:16 | 45953.5528 | 2025-10-23 15:14 | 45953.6347 | 0.022549 | 0.00019109 | 5 | 590 | Unplanned | Adverse Weather | Replace fuses
591 |  | 1991-26 | Ruatoria - Te Araroa | Gisborne | Hicks Bay 0102 | 2025-10-23 13:32 | 45953.5639 | 2025-10-23 13:42 | 45953.5708 | 0.098987 | 0.0098987 | 259 | 2590 | Unplanned | Defective Equipment | Broken binder at 50 kV pole J1775
592 |  | 1991-26 | Ruatoria - Te Araroa | Gisborne | Te Araroa 0103 | 2025-10-23 13:32 | 45953.5639 | 2025-10-23 13:42 | 45953.5708 | 0.048156 | 0.0048156 | 126 | 1260 | Unplanned | Defective Equipment | Broken binder at 50 kV pole J1775
593 |  | 1991-26 | Ruatoria - Te Araroa | Gisborne | Awatere 0101 | 2025-10-23 13:32 | 45953.5639 | 2025-10-23 13:37 | 45953.5674 | 0.017199 | 0.0034397 | 90 | 450 | Unplanned | Defective Equipment | Broken binder at 50 kV pole J1775
594 |  | 1991-26 | Ruatoria - Te Araroa | Gisborne | Te Araroa LS 0120 | 2025-10-23 13:32 | 45953.5639 | 2025-10-23 13:42 | 45953.5708 | 0.00038219 | 3.8219e-05 | 1 | 10 | Unplanned | Defective Equipment | Broken binder at 50 kV pole J1775
595 |  | 1992-26 | Parkinson Street | Gisborne | Solander 0706 | 2025-10-23 14:09 | 45953.5896 | 2025-10-23 15:56 | 45953.6639 | 0.076476 | 0.0029046 | 76 | 2001 | Unplanned | Defective Equipment | HV cable blew up in RMS B993
596 |  | 1993-26 | Awamate Road | Wairoa | Raupunga 3101 | 2025-10-23 15:01 | 45953.6257 | 2025-10-23 15:44 | 45953.6556 | 0.019721 | 0.00045863 | 12 | 516 | Unplanned | Defective Equipment | Broken conductor at pole W6129 repaired
597 |  | 1994-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-10-23 15:32 | 45953.6472 | 2025-10-23 17:24 | 45953.725 | 0.3095 | 0.0082553 | 216 | 8098 | Unplanned | Adverse Weather | No fault located. Circuit returned to normal after high winds.
598 |  | 6159-26 | 1916 Ruapapa Road, Tuai | Wairoa | Raupunga 3101 | 2025-10-23 15:42 | 45953.6542 | 2025-10-23 17:07 | 45953.7132 | 0.035735 | 0.00042041 | 11 | 935 | Unplanned | Adverse Weather | Replace fuses
599 |  | 6160-26 | 73 Brownlie Rd Frasertown | Wairoa | Frasertown 3103 | 2025-10-23 17:38 | 45953.7347 | 2025-10-23 22:10 | 45953.9236 | 0.031187 | 0.00011466 | 3 | 816 | Unplanned | Adverse Weather | Replace fuses
600 |  | 6161-26 | 978 Paparatu Road | Gisborne | Te Arai 0906 | 2025-10-23 18:49 | 45953.784 | 2025-10-23 21:15 | 45953.8854 | 0.0837 | 0.00057328 | 15 | 2190 | Unplanned | Unknown cause | Replace fuses
601 |  | 1996-26 | Matawai, Te Wera, Rakauroa, Motu | Gisborne | Matawai 1204 | 2025-10-23 19:42 | 45953.8208 | 2025-10-24 13:23 | 45954.5576 | 0.4662 | 0.0088286 | 231 | 12198 | Unplanned | Adverse Weather | Sectionaliser F423 open after E/F trip on CB F408. Line patrolled by helicopter, no apparent cause. Suspect line clash due to high wind.
602 |  | 1995-26 | Whangara Road, Wharf Road | Gisborne | Rototahi 0403 | 2025-10-23 19:53 | 45953.8285 | 2025-10-23 22:43 | 45953.9465 | 0.44728 | 0.004892 | 128 | 11703 | Unplanned | Defective Equipment | HV conductor down at pole G1134
603 |  | 6162-26 | 770 Tutamoe Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2025-10-24 07:09 | 45954.2979 | 2025-10-24 11:09 | 45954.4646 | 0.1009 | 0.00042041 | 11 | 2640 | Unplanned | Adverse Weather | Replace fuses
604 |  | 6163-26 | 335 Takapau Road, Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2025-10-24 07:23 | 45954.3076 | 2025-10-24 09:09 | 45954.3812 | 0.03241 | 0.00030575 | 8 | 848 | Unplanned | Adverse Weather | Replace fuses
605 |  | 3842-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-10-24 08:31 | 45954.3549 | 2025-10-24 15:14 | 45954.6347 | 0.86253 | 0.0021403 | 56 | 11308.1507 | Planned | Planned | Replace HV Poles
606 |  | 6164-26 | 535 Matahiia Road, Raukumara | Gisborne | Makarika 0204 | 2025-10-24 14:04 | 45954.5861 | 2025-10-24 17:13 | 45954.7174 | 0.065011 | 0.00034397 | 9 | 1701 | Unplanned | Adverse Weather | Replace fuses
607 |  | 1997-26 | Arakihi Road | Gisborne | Tauwhareparae 0404 | 2025-10-24 16:45 | 45954.6979 | 2025-10-25 09:12 | 45955.3833 | 0.3395 | 0.00034397 | 9 | 8883 | Unplanned | Vegetation | Tree through line at pole G1625. Left isolated overnight as too dark to complete work safely.
608 |  | 6165-26 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2025-10-26 12:36 | 45956.525 | 2025-10-26 15:40 | 45956.6528 | 0.056258 | 0.00030575 | 8 | 1472 | Unplanned | Unknown cause | Replace fuses
609 |  | 1998-26 | Hihiroroa Road South, Totangi Road | Gisborne | Totangi 1101 | 2025-10-27 13:41 | 45957.5701 | 2025-10-29 13:12 | 45959.55 | 0.73598 | 0.0038601 | 101 | 19257 | Unplanned | Vegetation | Tree tangled in HV conductor between D468 - D4001 due to strong wind
610 |  | 6166-26 | 7 Kaitawa Road, Tuai | Wairoa | Village 2002 | 2025-10-27 15:50 | 45957.6597 | 2025-10-27 17:30 | 45957.7292 | 0.2102 | 0.002102 | 55 | 5500 | Unplanned | Adverse Weather | Replace fuses
611 |  | 1999-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-10-27 15:57 | 45957.6646 | 2025-10-27 19:22 | 45957.8069 | 0.17237 | 0.00084082 | 22 | 4510 | Unplanned | Vegetation | Tree through HV conductor between poles E2892-E2894
612 |  | 6167-26 | 597 Waihau Rd | Gisborne | Rototahi 0403 | 2025-10-27 17:49 | 45957.7424 | 2025-10-27 19:00 | 45957.7917 | 0.03799 | 0.00053507 | 14 | 994 | Unplanned | Adverse Weather | Replace fuses
613 |  | 1000-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-10-27 17:56 | 45957.7472 | 2025-10-28 09:53 | 45958.4118 | 2.0699 | 0.0054271 | 142 | 54159 | Unplanned | Adverse Weather | Adverse weather. Suspect line clash due to strong wind.
614 |  | 1001-26 | Whakarau Road | Gisborne | Matawai 1204 | 2025-10-27 18:41 | 45957.7785 | 2025-10-28 17:17 | 45958.7201 | 1.9398 | 0.0024078 | 63 | 50754 | Unplanned | Defective Equipment | Conductor down at F2282
615 |  | 1002-26 | Taumata Road, Waimaha Road | Gisborne | Tahora 1103 | 2025-10-27 19:25 | 45957.809 | 2025-10-28 14:08 | 45958.5889 | 1.0286 | 0.0024078 | 63 | 26913 | Unplanned | Defective Equipment | Conductor down D1300 - D1301
616 |  | 1003-26 | Motu | Gisborne | Matawai 1204 | 2025-10-27 19:59 | 45957.8326 | 2025-10-28 17:53 | 45958.7451 | 1.1946 | 0.0080642 | 211 | 31257 | Unplanned | Vegetation | Trees brought down HV conductors
617 |  | 1014-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-10-27 20:05 | 45957.8368 | 2025-10-28 17:39 | 45958.7354 | 0.34619 | 0.00026753 | 7 | 9058 | Unplanned | Adverse Weather | Patrolled beyond HV fuses E1107 (2 blown). No obvious fault.
618 |  | 1004-26 | Whatatutu | Gisborne | Whatatutu 1201 | 2025-10-27 21:18 | 45957.8875 | 2025-10-28 07:04 | 45958.2944 | 0.56576 | 0.0029046 | 76 | 14803 | Unplanned | Adverse Weather | No fault found. Suspect line clash due to strong wind.
619 |  | 1005-26 | Bushy Knoll | Gisborne | Tiniroto 1003 | 2025-10-27 21:43 | 45957.9049 | 2025-10-28 13:19 | 45958.5549 | 0.34947 | 0.00042041 | 11 | 9144 | Unplanned | Defective Equipment | Conductor down from D3698 - D3699
620 |  | 1006-26 | Waimata feeder | Gisborne | Waimata 0903 | 2025-10-28 00:55 | 45958.0382 | 2025-10-28 09:20 | 45958.3889 | 9.5995 | 0.04999 | 1308 | 251172 | Unplanned | Adverse Weather | Adverse weather. Suspect line clash due to strong wind. Note Transpower outage occurred during this outage, affecting restoration times.
621 |  | 1008-26 | Raupunga, Kotemaori | Wairoa | Raupunga 3101 | 2025-10-28 05:27 | 45958.2271 | 2025-10-29 09:54 | 45959.4125 | 1.242 | 0.0099752 | 261 | 32496 | Unplanned | Vegetation | Tree through HV lines at poles W580 - W5221 during high winds
622 |  | 6168-26 | 73 Brownlie Road, Frasertown | Wairoa | Frasertown 3103 | 2025-10-28 07:19 | 45958.3049 | 2025-10-29 17:30 | 45959.7292 | 0.23516 | 0.00011466 | 3 | 6153 | Unplanned | Vegetation | Replace fuses
623 |  | 6170-26 | 12 Okare Rd , Ohuka | Wairoa | Ruakituri 2003 | 2025-10-28 07:35 | 45958.316 | 2025-10-28 12:05 | 45958.5035 | 0.25798 | 0.00095547 | 25 | 6750 | Unplanned | Adverse Weather | Replace fuses
624 |  | 6171-26 | 120 Mangaroa Rd , Ruakaturi | Wairoa | Ruakituri 2003 | 2025-10-28 07:36 | 45958.3167 | 2025-10-28 13:45 | 45958.5729 | 0.028206 | 7.6438e-05 | 2 | 738 | Unplanned | Adverse Weather | Replace fuses
625 |  | 1009-26 | Frasertown Road | Wairoa | Nuhaka 3203 | 2025-10-28 07:47 | 45958.3243 | 2025-10-28 12:46 | 45958.5319 | 0.65026 | 0.0076438 | 200 | 17014 | Unplanned | Third Party Interference | Length of fencing wire across Kiwi B conductor at pole W1759-W6731. Burnt conductor down on double circuit pole shared with Nuhaka feeder.
626 |  | 6169-26 | 159 Kokako Road, Tuai | Wairoa | Morere 3401 | 2025-10-28 08:05 | 45958.3368 | 2025-10-28 10:35 | 45958.441 | 0.057328 | 0.00038219 | 10 | 1500 | Unplanned | Adverse Weather | Replace fuses
627 |  | 1011-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-10-28 11:54 | 45958.4958 | 2025-10-28 12:26 | 45958.5181 | 0.068488 | 0.0021403 | 56 | 1792 | Unplanned | Defective Equipment | Blown jumper at pole D4340
628 |  | 1015-26 | Waitahaia | Gisborne | Mata 0304 | 2025-10-28 14:21 | 45958.5979 | 2025-10-29 15:36 | 45959.65 | 0.40531 | 0.00026753 | 7 | 10605 | Unplanned | Defective Equipment | Broken conductor between H4497 - H4498
629 |  | 1013-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2025-10-28 16:34 | 45958.6903 | 2025-10-28 19:21 | 45958.8063 | 0.20466 | 0.0017963 | 47 | 5355 | Unplanned | Defective Equipment | Conductor down D2686 - D2687. Suspect conductor clash due to wind.
630 |  | 1018-26 | Horehore Road | Gisborne | Makarika 0204 | 2025-10-29 07:02 | 45959.2931 | 2025-10-30 13:31 | 45960.5632 | 0.35483 | 0.00038219 | 10 | 9284 | Unplanned | Defective Equipment | Replace pole H1532, cross arm on the ground
631 |  | 6173-26 | 888 Kakariki Rd, Kotemaori | Wairoa | Raupunga 3101 | 2025-10-29 07:14 | 45959.3014 | 2025-10-29 10:15 | 45959.4271 | 0.013835 | 7.6438e-05 | 2 | 362 | Unplanned | Lightning | Replace fuses
632 |  | 1017-26 | Tunanui Road | Wairoa | Mahia 3301 | 2025-10-29 07:48 | 45959.325 | 2025-10-30 12:05 | 45960.5035 | 0.454 | 0.00026753 | 7 | 11879 | Unplanned | Defective Equipment | Burnt 11 kV pole W9602 caused by broken binder due to high winds
633 |  | 6174-26 | 267 Kokako Rd , Tuai | Wairoa | Village 2002 | 2025-10-29 08:49 | 45959.3674 | 2025-10-29 14:12 | 45959.5917 | 0.037034 | 0.00011466 | 3 | 969 | Unplanned | Lightning | Replace fuses
634 |  | 3876-26 | Oswald Street | Gisborne | Aberdeen 0609 | 2025-10-29 09:04 | 45959.3778 | 2025-10-29 15:19 | 45959.6382 | 3.5544 | 0.0094783 | 248 | 46940.7414 | Planned | Planned | Isolation for tree cutting
635 |  | 1016-26 | Rakauroa Road | Gisborne | Matawai 1204 | 2025-10-29 10:18 | 45959.4292 | 2025-10-30 12:54 | 45960.5375 | 0.11202 | 0.00068794 | 18 | 2931 | Unplanned | Defective Equipment | Conductor down between red tagged poles F684 - F685. Poles replaced and conductor repaired.
636 |  | 6175-26 | 237 Swarbrick Rd | Gisborne | Matawai 1204 | 2025-10-29 14:49 | 45959.6174 | 2025-10-29 18:30 | 45959.7708 | 0.042232 | 0.00019109 | 5 | 1105 | Unplanned | Adverse Weather | Replace fuses
637 |  | 6176-26 | 353 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-10-29 14:55 | 45959.6215 | 2025-10-29 16:33 | 45959.6896 | 0.0074909 | 7.6438e-05 | 2 | 196 | Unplanned | Unknown cause | Replaced blown Hv/lv fuse @ TxE117
638 |  | 6177-26 | 599,1180 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2025-10-29 17:30 | 45959.7292 | 2025-10-30 10:35 | 45960.441 | 0.35257 | 0.00034397 | 9 | 9225 | Unplanned | Unknown cause | Replace fuses
639 |  | 6172-26 | 58 Taihamiti Rd | Gisborne | Whatatutu 1201 | 2025-10-29 17:40 | 45959.7361 | 2025-10-29 19:30 | 45959.8125 | 0.0084082 | 7.6438e-05 | 2 | 220 | Unplanned | Unknown cause | Replace fuses
640 |  | 6178-26 | 6307 Matawai Rd | Gisborne | Matawai 1204 | 2025-10-29 19:09 | 45959.7979 | 2025-10-29 21:30 | 45959.8958 | 0.010778 | 7.6438e-05 | 2 | 282 | Unplanned | Wildlife | Replace fuses
641 |  | 6179-26 | 3237 Putere Rd, Raupunga | Wairoa | Raupunga 3101 | 2025-10-30 07:45 | 45960.3229 | 2025-10-30 11:22 | 45960.4736 | 0.016587 | 7.6438e-05 | 2 | 434 | Unplanned | Lightning | Replace fuses
642 |  | 3877-26 | Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-10-30 08:34 | 45960.3569 | 2025-10-30 13:44 | 45960.5722 | 0.047392 | 0.00015288 | 4 | 620.1192 | Planned | Planned | Isolation to cut trees
643 |  | 3917-26 | Solander Street | Gisborne | Solander 0706 | 2025-10-30 08:37 | 45960.359 | 2025-10-30 17:20 | 45960.7222 | 0.099943 | 0.00019109 | 5 | 2615 | Planned | Planned | Planned outage after cable fault on SW 1992A
644 |  | 3874-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-10-30 09:04 | 45960.3778 | 2025-10-30 14:01 | 45960.584 | 0.24972 | 0.00084082 | 22 | 3269.7747 | Planned | Planned | Replace TX E80 structure
645 |  | 1019-26 | Totangi Road | Gisborne | Ngatapa 1102 | 2025-10-30 11:48 | 45960.4917 | 2025-10-30 16:11 | 45960.6743 | 0.010052 | 3.8219e-05 | 1 | 263 | Unplanned | Defective Equipment | Replace faulty transformer D63
646 |  | 3883-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-02 08:04 | 45963.3361 | 2025-11-02 16:08 | 45963.6722 | 0.20348 | 0.00042041 | 11 | 2663.1191 | Planned | Planned | Install New 11kV fuses on Pole J2703 and replace 11kV poles
647 |  | 6180-26 | 396 Stafford Road | Gisborne | Tahunga 1004 | 2025-11-02 08:52 | 45963.3694 | 2025-11-02 09:55 | 45963.4132 | 0.016855 | 0.00026753 | 7 | 441 | Unplanned | Unknown cause | Replace Fuses
648 |  | 1021-26 | Aberdeen Rd / Ballance St | Gisborne | Aberdeen 0609 | 2025-11-02 18:24 | 45963.7667 | 2025-11-02 21:20 | 45963.8889 | 3.0481 | 0.05515 | 1443 | 79754 | Unplanned | Defective Equipment | Aberdeen Feeder CB B825 L/our A-phase o/c. No faults were located after sectionalise switching
649 |  | 1022-26 | Wharekopae Road | Gisborne | Muriwai 0905 | 2025-11-02 23:17 | 45963.9701 | 2025-11-03 14:21 | 45964.5979 | 0.10365 | 0.00011466 | 3 | 2712 | Unplanned | Third Party Interference | Broken LV Pole C1362 due to Car Vs pole
650 |  | 6181-26 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2025-11-03 06:08 | 45964.2556 | 2025-11-03 10:32 | 45964.4389 | 0.080719 | 0.00030575 | 8 | 2112 | Unplanned | Unknown cause | Replace Fuses
651 |  | 6182-26 | 396 Stafford Road | Gisborne | Tahunga 1004 | 2025-11-03 06:16 | 45964.2611 | 2025-11-03 08:17 | 45964.3451 | 0.032371 | 0.00026753 | 7 | 847 | Unplanned | Unknown cause | Replace Fuses
652 |  | 3884-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-03 08:03 | 45964.3354 | 2025-11-03 15:45 | 45964.6562 | 0.017657 | 3.8219e-05 | 1 | 231.0088 | Planned | Planned | Replace 11kV Red Tag Poles J2720 & J2721
653 |  | 1023-26 | Putere Road | Wairoa | Raupunga 3101 | 2025-11-03 10:22 | 45964.4319 | 2025-11-03 11:50 | 45964.4931 | 0.0067265 | 7.6438e-05 | 2 | 176 | Unplanned | Defective Equipment | To replace burnt LV fuse holder at TX W354
654 |  | 3886-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-04 08:03 | 45965.3354 | 2025-11-04 16:13 | 45965.6757 | 0.206 | 0.00042041 | 11 | 2696.133 | Planned | Planned | Replace 11kV Red Tag Poles J2684 & J2685
655 |  | 3895-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-11-04 08:31 | 45965.3549 | 2025-11-04 15:00 | 45965.625 | 0.29505 | 0.00076438 | 20 | 3862.0174 | Planned | Planned | To replace 50kV Pole E2327
656 |  | 3865-26 | Mangone Road | Wairoa | Morere 3401 | 2025-11-04 08:37 | 45965.359 | 2025-11-04 15:11 | 45965.6326 | 0.1807 | 0.00045863 | 12 | 2365.0842 | Planned | Planned | Replace HV Poles
657 |  | 3870-26 | Russell Road | Gisborne | Ngatapa 1102 | 2025-11-04 09:05 | 45965.3785 | 2025-11-04 11:49 | 45965.4924 | 0.068947 | 0.00042041 | 11 | 902.6937 | Planned | Planned | Replace 11kV pole D4129
658 |  | 1025-26 | Nuhaka - Opoutama Road | Wairoa | Morere 3401 | 2025-11-04 11:58 | 45965.4986 | 2025-11-04 14:45 | 45965.6146 | 0.082973 | 0.00049685 | 13 | 2171 | Unplanned | Third Party Interference | Resident cut down tree - went through LV conductor on Road @ Pole W8495
659 |  | 1026-26 | Ruakituri Rd / Papuni Road | Wairoa | Ruakituri 2003 | 2025-11-04 13:47 | 45965.5743 | 2025-11-05 20:58 | 45966.8736 | 1.4478 | 0.0047009 | 123 | 37882 | Unplanned | Third Party Interference | Truck brought down HV lines betwn Pole W7362 - W21863 & also broke HV Pole W7362
660 |  | 1027-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-11-04 15:23 | 45965.641 | 2025-11-04 16:35 | 45965.691 | 0.022014 | 0.00030575 | 8 | 576 | Unplanned | Defective Equipment | To repair 400V lines between poles D4329 - D4330
661 |  | 3871-26 | Hillside Road | Gisborne | Ngatapa 1102 | 2025-11-05 09:05 | 45966.3785 | 2025-11-05 13:44 | 45966.5722 | 0.021326 | 7.6438e-05 | 2 | 279.0229 | Planned | Planned | Replace HV Pole D4927
662 |  | 6183-26 | 1836 Wharerata Road | Gisborne | Muriwai 0905 | 2025-11-05 11:09 | 45966.4646 | 2025-11-05 12:13 | 45966.509 | 0.002446 | 3.8219e-05 | 1 | 64 | Unplanned | Unknown cause | Possible LV clash from bull rubbing against LV pole
663 |  | 3888-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-06 08:02 | 45967.3347 | 2025-11-06 16:23 | 45967.6826 | 0.019148 | 3.8219e-05 | 1 | 250.5096 | Planned | Planned | Replace HV Poles
664 |  | 3866-26 | Mangone Valley Road | Wairoa | Morere 3401 | 2025-11-06 08:32 | 45967.3556 | 2025-11-06 13:58 | 45967.5819 | 0.59996 | 0.0031722 | 83 | 13742.9906 | Planned | Planned | To replace 11kV pole and install new 11kV Pole midspan betwn W1059-W8045. Note: 71 Customers advertised under ref #3925
665 |  | 3897B-26 | Christopher Road | Gisborne | Dalton 0502 | 2025-11-06 09:18 | 45967.3875 | 2025-11-06 15:18 | 45967.6375 | 0.12383 | 0.00034397 | 9 | 1620.5572 | Planned | Planned | Replace HV Poles
666 |  | 6184-26 | 90 Bellarby Road | Gisborne | W O Kuri 1001 | 2025-11-07 05:40 | 45968.2361 | 2025-11-07 07:44 | 45968.3222 | 0.033174 | 0.00026753 | 7 | 868 | Unplanned | Unknown cause | Replace Fuses
667 |  | 3889-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-07 08:01 | 45968.334 | 2025-11-07 16:11 | 45968.6743 | 0.018727 | 3.8219e-05 | 1 | 245.0094 | Planned | Planned | Replace HV Poles
668 |  | 3872-26 | Parikanapa Road | Gisborne | Parikanapa 1002 | 2025-11-07 09:03 | 45968.3771 | 2025-11-07 13:24 | 45968.5583 | 0.10973 | 0.00042041 | 11 | 1436.263 | Planned | Planned | Replace Poles
669 |  | 3905-26 | Balance St / Barkers Hill | Gisborne | Aberdeen 0609 | 2025-11-07 09:03 | 45968.3771 | 2025-11-07 10:06 | 45968.4208 | 0.14206 | 0.0022549 | 59 | 1685.2916 | Planned | Planned | To Replace 11kV standoff insulators
670 |  | 3899-26 | Mata Road | Gisborne | Mata 0304 | 2025-11-07 09:32 | 45968.3972 | 2025-11-07 12:22 | 45968.5153 | 0.084464 | 0.00049685 | 13 | 1105.9689 | Planned | Planned | To replace 11kV Poles H4416 & H781
671 |  | 3891-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-08 08:02 | 45969.3347 | 2025-11-08 15:04 | 45969.6278 | 0.016128 | 3.8219e-05 | 1 | 211.0081 | Planned | Planned | Replace red tag poles
672 |  | 3878-26 | Mangaturanga Road | Wairoa | Raupunga 3101 | 2025-11-08 10:04 | 45969.4194 | 2025-11-08 13:06 | 45969.5458 | 1.155 | 0.0065354 | 171 | 15145.7622 | Planned | Planned | Install new 11mt Busk with new single ph TX
673 |  | 1030-26 | Frasertown Feeder | Wairoa | Frasertown 3103 | 2025-11-08 18:19 | 45969.7632 | 2025-11-08 18:29 | 45969.7701 | 0.18574 | 0.018574 | 486 | 4860 | Unplanned | Third Party Interference | Isolate line for Fire & Emergency
674 |  | 1029-26 | Waimata Valley Road | Gisborne | Waimata 0903 | 2025-11-08 18:52 | 45969.7861 | 2025-11-09 07:09 | 45970.2979 | 0.52715 | 0.0030575 | 80 | 13793 | Unplanned | Vegetation | Tree through 11kV lines betwn Poles E310 - E1049
675 |  | 6185-26 | 109 Stevens Road | Gisborne | Dalton 0502 | 2025-11-09 06:07 | 45970.2549 | 2025-11-09 09:40 | 45970.4028 | 0.056985 | 0.00026753 | 7 | 1491 | Unplanned | Unknown cause | Replace Fuses
676 |  | 6186-26 | 23 Mangaoae Road | Gisborne | Kanakanaia 1202 | 2025-11-09 08:07 | 45970.3382 | 2025-11-09 10:15 | 45970.4271 | 0.0097841 | 7.6438e-05 | 2 | 256 | Unplanned | Defective Equipment | Faulty TX, only one phase working, jumpered house onto good phase. Reported to manager to change TX
677 |  | 6187-26 | 16 Mangaoae Road | Gisborne | Kanakanaia 1202 | 2025-11-09 18:18 | 45970.7625 | 2025-11-09 19:45 | 45970.8229 | 0.0266 | 0.00030575 | 8 | 696 | Unplanned | Unknown cause | Replace Fuses
678 |  | 3892-26 | Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-10 08:04 | 45971.3361 | 2025-11-10 15:29 | 45971.6451 | 0.18708 | 0.00042041 | 11 | 2448.529 | Planned | Planned | Replace 11kV Poles
679 |  | 6188-26 | 2704 Mahia East Coast Road | Wairoa | Mahia 3301 | 2025-11-10 15:31 | 45971.6465 | 2025-11-10 18:23 | 45971.766 | 0.013147 | 7.6438e-05 | 2 | 344 | Unplanned | Unknown cause | 1 blown HV TX fuse 3amp
680 |  | 6189-26 | 1124 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-11-11 06:34 | 45972.2736 | 2025-11-11 08:56 | 45972.3722 | 0.22251 | 0.001567 | 41 | 5822 | Unplanned | Unknown cause | Replace Fuses
681 |  | 1032-26 | Te Araroa Sub | Gisborne | Awatere 0101 | 2025-11-11 07:41 | 45972.3201 | 2025-11-11 08:08 | 45972.3389 | 0.092872 | 0.0034397 | 90 | 2430 | Unplanned | Defective Equipment | Burnt 50kV Pole J1875 on Ruatoria - Te Araroa 50kV Line
682 |  | 1032-26 | Te Araroa Sub | Gisborne | Te Araroa 0103 | 2025-11-11 07:41 | 45972.3201 | 2025-11-11 08:43 | 45972.3632 | 0.29857 | 0.0048156 | 126 | 7812 | Unplanned | Defective Equipment | Burnt 50kV Pole J1875 on Ruatoria - Te Araroa 50kV Line
683 |  | 1032-26 | Te Araroa Sub | Gisborne | Hicks Bay 0102 | 2025-11-11 07:41 | 45972.3201 | 2025-11-11 08:48 | 45972.3667 | 0.62538 | 0.0098987 | 259 | 16363 | Unplanned | Defective Equipment | Burnt 50kV Pole J1875 on Ruatoria - Te Araroa 50kV Line
684 |  | 1032-26 | Te Araroa Sub | Gisborne | Te Araroa LS 0120 | 2025-11-11 07:41 | 45972.3201 | 2025-11-11 08:43 | 45972.3632 | 0.0023696 | 3.8219e-05 | 1 | 62 | Unplanned | Defective Equipment | Burnt 50kV Pole J1875 on Ruatoria - Te Araroa 50kV Line
685 |  | 3900-26 | Koranga Valley Road | Gisborne | Matawai 1204 | 2025-11-11 09:03 | 45972.3771 | 2025-11-11 14:22 | 45972.5986 | 0.31699 | 0.00099369 | 26 | 4151.2629 | Planned | Planned | Replace 11kV Poles F1644 & F1645
686 |  | 3902-26 | Mata Road | Gisborne | Mata 0304 | 2025-11-11 09:06 | 45972.3792 | 2025-11-11 13:20 | 45972.5556 | 0.0097076 | 3.8219e-05 | 1 | 127.0057 | Planned | Planned | Replace 11kV Poles H1061 & H1060
687 |  | 1033-26 | Mangaharei Street | Gisborne | Ruatoria 0201 | 2025-11-11 13:05 | 45972.5451 | 2025-11-11 13:16 | 45972.5528 | 0.019339 | 0.0017581 | 46 | 506 | Unplanned | Lightning | To reload and close blown HV fuses TX J87
688 |  | 6190-26 | 1911 Putere Road | Wairoa | Raupunga 3101 | 2025-11-11 15:16 | 45972.6361 | 2025-11-11 17:24 | 45972.725 | 0.0097841 | 7.6438e-05 | 2 | 256 | Unplanned | Unknown cause | Replace Fuses
689 |  | 3903-26 | Tuai Main Road | Wairoa | Village 2002 | 2025-11-12 08:02 | 45973.3347 | 2025-11-12 18:29 | 45973.7701 | 1.503 | 0.0024078 | 63 | 16021.5026 | Planned | Planned | Install new RMU W1330-W1333 beside existing RMU W1449
690 |  | 1034-26 | Whakaangiangi Road, Te Araroa | Gisborne | Awatere 0101 | 2025-11-12 12:28 | 45973.5194 | 2025-11-14 12:30 | 45975.5208 | 0.79885 | 0.018154 | 475 | 20902 | Unplanned | Defective Equipment | To replace burnt HV cross arm at pole J3025
691 |  | 1035-26 | Tauwhareparae | Gisborne | Tauwhareparae 0404 | 2025-11-12 23:45 | 45973.9896 | 2025-11-13 14:15 | 45974.5938 | 3.4151 | 0.0053507 | 140 | 89357 | Unplanned | Adverse Environment | River caused slip, brought tree into contact with line @ G302-G1793
692 |  | 1036-26 | Mata Road | Gisborne | Mata 0304 | 2025-11-13 00:19 | 45974.0132 | 2025-11-14 14:45 | 45975.6146 | 1.3239 | 0.0021403 | 56 | 34641 | Unplanned | Defective Equipment | Broken HV Pole H1088 due to wind
693 |  | 3906-26 | Tuai Main Road | Wairoa | Village 2002 | 2025-11-13 08:06 | 45974.3375 | 2025-11-13 14:49 | 45974.6174 | 0.43126 | 0.0010701 | 28 | 5648.0377 | Planned | Planned | Install new RMU W1333
694 |  | 1037-26 | Matawai Road | Gisborne | Te Karaka 1203 | 2025-11-13 08:50 | 45974.3681 | 2025-11-13 13:58 | 45974.5819 | 0.023543 | 7.6438e-05 | 2 | 616 | Unplanned | Defective Equipment | To repair broken LV conductor betwn pole E1776-E1777
695 |  | 3901-26 | Koranga Valley Road | Gisborne | Matawai 1204 | 2025-11-13 09:05 | 45974.3785 | 2025-11-13 14:04 | 45974.5861 | 0.29711 | 0.00099369 | 26 | 3891.2629 | Planned | Planned | Replace Poles
696 |  | 6191-26 | 7083 Matawai Road | Gisborne | Matawai 1204 | 2025-11-13 16:39 | 45974.6937 | 2025-11-13 19:41 | 45974.8201 | 0.0069559 | 3.8219e-05 | 1 | 182 | Unplanned | Lightning | Replace Fuses
697 |  | 6192-26 | 172 Koranga Valley Road | Gisborne | Matawai 1204 | 2025-11-13 17:12 | 45974.7167 | 2025-11-13 20:15 | 45974.8438 | 0.020982 | 0.00011466 | 3 | 549 | Unplanned | Lightning | Replace Fuses
698 |  | 1043-26 | Makarika | Gisborne | Makarika 0204 | 2025-11-14 05:15 | 45975.2188 | 2025-11-15 18:03 | 45976.7521 | 0.56465 | 0.0025607 | 67 | 14774 | Unplanned | Lightning | Blown TX due to Lightning
699 |  | 3912-26 | Koranga Valley Road | Gisborne | Matawai 1204 | 2025-11-14 09:09 | 45975.3812 | 2025-11-14 13:00 | 45975.5417 | 0.22954 | 0.00099369 | 26 | 3007.2629 | Planned | Planned | Replace 11kV Poles
700 |  | 6193-26 | 1984 Matawai Road | Gisborne | Te Karaka 1203 | 2025-11-14 10:52 | 45975.4528 | 2025-11-14 12:32 | 45975.5222 | 0.0076438 | 7.6438e-05 | 2 | 200 | Unplanned | Unknown cause | Replace Fuses
701 |  | 1038-26 | Tuai 11kV Sub | Wairoa | Village 2002 | 2025-11-14 13:04 | 45975.5444 | 2025-11-14 13:13 | 45975.5507 | 0.060195 | 0.0066883 | 175 | 1575 | Unplanned | Lightning | Restore Tuai 11kV Sub after lightning strike
702 |  | 1038-26 | Tuai 11kV Sub | Wairoa | Lake 2001 | 2025-11-14 13:04 | 45975.5444 | 2025-11-14 13:13 | 45975.5507 | 0.0027518 | 0.00030575 | 8 | 72 | Unplanned | Lightning | Restore Tuai 11kV Sub after lightning strike
703 |  | 1038-26 | Tuai 11kV Sub | Wairoa | Ruakituri 2003 | 2025-11-14 13:04 | 45975.5444 | 2025-11-14 13:13 | 45975.5507 | 0.053315 | 0.0059239 | 155 | 1395 | Unplanned | Lightning | Restore Tuai 11kV Sub after lightning strike
704 |  | 1038-26 | Tuai 11kV Sub | Wairoa | Genesis 2004 | 2025-11-14 13:04 | 45975.5444 | 2025-11-14 13:13 | 45975.5507 | 0.00034397 | 3.8219e-05 | 1 | 9 | Unplanned | Lightning | Restore Tuai 11kV Sub after lightning strike
705 |  | 6194-26 | Otoi Road | Wairoa | Raupunga 3101 | 2025-11-14 16:00 | 45975.6667 | 2025-11-14 16:30 | 45975.6875 | 0.0022931 | 7.6438e-05 | 2 | 60 | Unplanned | Lightning | Replace Fuses
706 |  | 6197-26 | 2880 Mangapoike Road | Wairoa | Frasertown 3103 | 2025-11-14 16:29 | 45975.6868 | 2025-11-14 19:55 | 45975.8299 | 0.11022 | 0.00053507 | 14 | 2884 | Unplanned | Lightning | Replace Fuses
707 |  | 6195-26 | Otoi & Smyth Road cell site | Wairoa | Raupunga 3101 | 2025-11-14 17:00 | 45975.7083 | 2025-11-14 17:16 | 45975.7194 | 0.0006115 | 3.8219e-05 | 1 | 16 | Unplanned | Lightning | Replace Fuses
708 |  | 6196-26 | 202 Otoi Road | Wairoa | Raupunga 3101 | 2025-11-14 17:28 | 45975.7278 | 2025-11-14 17:29 | 45975.7285 | 3.8219e-05 | 3.8219e-05 | 1 | 1 | Unplanned | Lightning | Replace Fuses
709 |  | 6198-26 | 711 Cricklewood Road | Wairoa | Raupunga 3101 | 2025-11-14 19:09 | 45975.7979 | 2025-11-14 21:30 | 45975.8958 | 0.010778 | 7.6438e-05 | 2 | 282 | Unplanned | Lightning | Replace Fuses
710 |  | 1039-26 | Whatatutu Road | Gisborne | Whatatutu 1201 | 2025-11-14 20:27 | 45975.8521 | 2025-11-15 15:24 | 45976.6417 | 0.51982 | 0.0029046 | 76 | 13601 | Unplanned | Lightning | To replace faulty transformer E186
711 |  | 6199-26 | Cricklewood Road | Wairoa | Raupunga 3101 | 2025-11-14 21:30 | 45975.8958 | 2025-11-14 22:00 | 45975.9167 | 0.0011466 | 3.8219e-05 | 1 | 30 | Unplanned | Lightning | Replace Fuses
712 |  | 6200-26 | Otoi Road | Wairoa | Raupunga 3101 | 2025-11-14 23:30 | 45975.9792 | 2025-11-14 23:40 | 45975.9861 | 0.00038219 | 3.8219e-05 | 1 | 10 | Unplanned | Lightning | Replace Fuses
713 |  | 1041-26 | Waipiro Bay | Gisborne | Inland 0301 | 2025-11-15 07:07 | 45976.2965 | 2025-11-16 12:00 | 45977.5 | 0.13247 | 7.6438e-05 | 2 | 3466 | Unplanned | Lightning | Lightning hit TX faulted
714 |  | 1040-26 | Bartletts | Gisborne | Muriwai 0905 | 2025-11-15 09:40 | 45976.4028 | 2025-11-15 12:40 | 45976.5278 | 0.42232 | 0.0051213 | 134 | 11050 | Unplanned | Defective Equipment | Found broken conductor unsure of cause
715 |  | 1044-26 | Otoi | Wairoa | Raupunga 3101 | 2025-11-15 12:27 | 45976.5188 | 2025-11-16 16:04 | 45977.6694 | 0.10537 | 0.00042041 | 11 | 2757 | Unplanned | Lightning | Blown TX due to Lightning
716 |  | 6201-26 | 680 Hereheretau Road | Wairoa | Nuhaka 3203 | 2025-11-15 14:02 | 45976.5847 | 2025-11-15 19:30 | 45976.8125 | 0.22564 | 0.00068794 | 18 | 5904 | Unplanned | Unknown cause | Replace Fuses
717 |  | 1042-26 | Te Reinga | Wairoa | Ruakituri 2003 | 2025-11-15 14:32 | 45976.6056 | 2025-11-15 21:04 | 45976.8778 | 0.51206 | 0.0078731 | 206 | 13398 | Unplanned | Vegetation | Trees in line tangled conductor
718 |  | 6202-26 | 1070 Taumata Road | Gisborne | Tahora 1103 | 2025-11-15 19:33 | 45976.8146 | 2025-11-15 21:35 | 45976.8993 | 0.0046627 | 3.8219e-05 | 1 | 122 | Unplanned | Unknown cause | Replace Fuses
719 |  | 3945-26 | Awamate Road | Wairoa | Frasertown 3103 | 2025-11-16 08:40 | 45977.3611 | 2025-11-16 12:27 | 45977.5188 | 0.043379 | 0.00019109 | 5 | 1135 | Planned | Planned | Lift x-arm & re-sag conductor
720 |  | 1045-26 | Tuakau Road | Gisborne | Mata 0304 | 2025-11-16 14:09 | 45977.5896 | 2025-11-16 18:29 | 45977.7701 | 0.014217 | 0.00057328 | 15 | 372 | Unplanned | Lightning | Lightning blew fuses at TX H139
721 |  | 6203-26 | 330 Shelton Road | Gisborne | Rototahi 0403 | 2025-11-17 08:57 | 45978.3729 | 2025-11-17 11:51 | 45978.4938 | 0.099752 | 0.00057328 | 15 | 2610 | Unplanned | Unknown cause | Replace Fuses
722 |  | 3880-26 | Te Araroa road | Gisborne | Awatere 0101 | 2025-11-17 09:02 | 45978.3764 | 2025-11-17 14:43 | 45978.6132 | 0.23459 | 0.00068794 | 18 | 3071.2289 | Planned | Planned | Isolating HV lines betwn J2374-J2412 to cut trees
723 |  | 3918-26 | Matawai Road | Gisborne | Te Karaka 1203 | 2025-11-17 10:00 | 45978.4167 | 2025-11-17 12:31 | 45978.5215 | 0.046169 | 0.00030575 | 8 | 604.2201 | Planned | Planned | Upgrade TX F370
724 |  | 3914-26 | Waimata Valley Road | Gisborne | Waimata 0903 | 2025-11-18 08:30 | 45979.3542 | 2025-11-18 13:58 | 45979.5819 | 0.12536 | 0.00038219 | 10 | 1640.6268 | Planned | Planned | To replace transformer structure E14
725 |  | 3919A-26 | Ihungia Road | Gisborne | Mata 0304 | 2025-11-18 08:32 | 45979.3556 | 2025-11-18 13:40 | 45979.5694 | 0.035314 | 0.00011466 | 3 | 462.0619 | Planned | Planned | Planned outage commenced - Tree felled thru line & fault - Gen installed to restore supply @ 13:40hrs. Recorded under SW1047.
726 |  | 3881-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2025-11-18 09:03 | 45979.3771 | 2025-11-18 14:06 | 45979.5875 | 0.046321 | 0.00015288 | 4 | 606.1101 | Planned | Planned | Isolate to cut trees at pole J2440
727 |  | 3908-26 | Anaura Road | Gisborne | Mata 0304 | 2025-11-18 09:03 | 45979.3771 | 2025-11-18 15:08 | 45979.6306 | 0.79515 | 0.0021785 | 57 | 10425.1617 | Planned | Planned | To replace 11kV poles G1438 & G1447
728 |  | 6204-26 | 287 SH 2 | Wairoa | Brickworks 3201 | 2025-11-18 10:54 | 45979.4542 | 2025-11-18 11:31 | 45979.4799 | 0.0084846 | 0.00022931 | 6 | 222 | Unplanned | Unknown cause | Replace Fuses
729 |  | 3915-26 | Goodwin Road | Gisborne | Whangara 0506 | 2025-11-19 08:32 | 45980.3556 | 2025-11-19 11:47 | 45980.491 | 0.022358 | 0.00011466 | 3 | 292.5568 | Planned | Planned | Replace 11kV poles
730 |  | 3882-26 | Awatere Road | Gisborne | Awatere 0101 | 2025-11-19 09:05 | 45980.3785 | 2025-11-19 13:40 | 45980.5694 | 0.042041 | 0.00015288 | 4 | 550.1101 | Planned | Planned | Cut Trees
731 |  | 3873-26 | Kokohu Road | Wairoa | Morere 3401 | 2025-11-19 09:06 | 45980.3792 | 2025-11-19 12:04 | 45980.5028 | 0.047621 | 0.00026753 | 7 | 1246 | Planned | Planned | Replace Red Tag Poles W8608
732 |  | 1048-26 | Bell Road | Gisborne | Bell 1406 | 2025-11-19 19:17 | 45980.8035 | 2025-11-19 20:56 | 45980.8722 | 0.69585 | 0.008905 | 233 | 18207 | Unplanned | Unknown cause | Bell Rd feeder CB18 open & locked out on inst o/c. Carried out sectionalised switching but no faults were found. Reports of heavy bang was heard at 32 Kemp Road
733 |  | 3913-26 | Titirangi Road | Wairoa | Frasertown 3103 | 2025-11-20 08:40 | 45981.3611 | 2025-11-20 13:40 | 45981.5694 | 0.18345 | 0.0006115 | 16 | 2401.7611 | Planned | Planned | To replace 11kV poles W4390 & W4391
734 |  | 3879A-26 | Waione Road & Te Araroa Road | Gisborne | Awatere 0101 | 2025-11-20 09:00 | 45981.375 | 2025-11-20 13:09 | 45981.5479 | 0.35211 | 0.0014141 | 37 | 4615.9179 | Planned | Planned | Isolate to cut trees near 11kV line
735 |  | 3909-26 | Anaura Road | Gisborne | Mata 0304 | 2025-11-20 09:04 | 45981.3778 | 2025-11-20 14:54 | 45981.6208 | 0.76247 | 0.0021785 | 57 | 9996.7304 | Planned | Planned | Replace 11kV poles G1452 & G1453
736 |  | 3926-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-11-20 09:08 | 45981.3806 | 2025-11-20 10:24 | 45981.4333 | 0.034856 | 0.00045863 | 12 | 456.2091 | Planned | Planned | To Re-strain 11kV line from Pole D3399 to D308
737 |  | 3954-26 | Matahiia Road | Gisborne | Makarika 0204 | 2025-11-20 09:08 | 45981.3806 | 2025-11-20 15:00 | 45981.625 | 0.12108 | 0.00034397 | 9 | 3168 | Planned | Planned | To Relocate HV pole H1658
738 |  | 6205-26 | 281 Kaiwaitau Road | Wairoa | Mahia 3301 | 2025-11-20 15:35 | 45981.6493 | 2025-11-20 17:36 | 45981.7333 | 0.009249 | 7.6438e-05 | 2 | 242 | Unplanned | Defective Equipment | DDO fuse wire rotted and broke
739 |  | 3910-26 | Anaura Road | Gisborne | Mata 0304 | 2025-11-21 09:00 | 45982.375 | 2025-11-21 13:28 | 45982.5611 | 0.58337 | 0.0021785 | 57 | 7650.4454 | Planned | Planned | Replace poles
740 |  | 1049-26 | Kopuawhara road | Wairoa | Mahia 3301 | 2025-11-21 09:11 | 45982.3826 | 2025-11-21 11:12 | 45982.4667 | 0.009249 | 7.6438e-05 | 2 | 242 | Unplanned | Vegetation | Cut trees on LV & HV line and repair LV wires
741 |  | 6206-26 | 338 Tuahu Road | Gisborne | Tauwhareparae 0404 | 2025-11-22 15:53 | 45983.6618 | 2025-11-22 17:22 | 45983.7236 | 0.0034015 | 3.8219e-05 | 1 | 89 | Unplanned | Unknown cause | Replace Fuses
742 |  | 1051-26 | Ohopo | Wairoa | Nuhaka 3203 | 2025-11-22 17:23 | 45983.7243 | 2025-11-22 19:22 | 45983.8069 | 0.031836 | 0.00026753 | 7 | 833 | Unplanned | Lightning | Replace faulty TX W116
743 |  | 6207-26 | 2507 Tiniroto road | Wairoa | Morere 3401 | 2025-11-23 15:47 | 45984.6576 | 2025-11-23 17:38 | 45984.7347 | 0.042423 | 0.00038219 | 10 | 1110 | Unplanned | Lightning | Replace Fuses
744 |  | 6208-26 | 3 Ruakituri Valley | Wairoa | Ruakituri 2003 | 2025-11-23 15:58 | 45984.6653 | 2025-11-23 17:53 | 45984.7451 | 0.043952 | 0.00038219 | 10 | 1150 | Unplanned | Lightning | Replace Fuses
745 |  | 1052-26 | Kaiti - Whataupoko | Gisborne | Whangara 0506 | 2025-11-23 19:42 | 45984.8208 | 2025-11-23 19:52 | 45984.8278 | 0.22587 | 0.022587 | 591 | 5910 | Unplanned | Lightning | Lightning Strike
746 |  | 1052-26 | Whangara Feeder | Gisborne | Whangara 0506 | 2025-11-23 19:42 | 45984.8208 | 2025-11-23 19:52 | 45984.8278 | 0.2125 | 0.02125 | 556 | 5560 | Unplanned | Lightning | Lightning
747 |  | 1053-26 | Shelley Road | Gisborne | Whangara 0506 | 2025-11-23 19:42 | 45984.8208 | 2025-11-27 09:26 | 45988.3931 | 0.39106 | 0.00279 | 73 | 10232 | Unplanned | Lightning | Switch hit by lightning failed
748 |  | 6209-26 | 1753 Whangara Road | Gisborne | Dalton 0502 | 2025-11-24 07:52 | 45985.3278 | 2025-11-24 10:15 | 45985.4271 | 0.0054653 | 3.8219e-05 | 1 | 143 | Unplanned | Lightning | Replace Fuses
749 |  | 6210-26 | 3960 State Highway 2 | Wairoa | Morere 3401 | 2025-11-24 08:47 | 45985.366 | 2025-11-24 10:38 | 45985.4431 | 0.0042423 | 3.8219e-05 | 1 | 111 | Unplanned | Lightning | Replace Fuses
750 |  | 1054-26 | Muriwai road | Gisborne | Muriwai 0905 | 2025-11-24 17:21 | 45985.7229 | 2025-11-25 17:23 | 45986.7243 | 1.7801 | 0.01074 | 281 | 46576 | Unplanned | Third Party Interference | Broken 11kV Pole C4882 due to car v's pole
751 |  | 3949-26 | Riverside Road | Gisborne | Whangara 0506 | 2025-11-25 09:02 | 45986.3764 | 2025-11-25 11:47 | 45986.491 | 0.025225 | 0.00015288 | 4 | 660 | Planned | Planned | Install new TX @ pole B2021
752 |  | 3911-26 | Anaura Road | Gisborne | Mata 0304 | 2025-11-25 09:05 | 45986.3785 | 2025-11-25 14:24 | 45986.6 | 0.69069 | 0.0021785 | 57 | 9054.4454 | Planned | Planned | Replace 11kV poles
753 |  | 3916-26 | Omana Road | Wairoa | Morere 3401 | 2025-11-25 09:08 | 45986.3806 | 2025-11-25 12:49 | 45986.534 | 0.084464 | 0.00038219 | 10 | 1105.4223 | Planned | Planned | Replace 11kv/400V Poles
754 |  | 6211-26 | 406 Waihi Road | Wairoa | Frasertown 3103 | 2025-11-25 10:16 | 45986.4278 | 2025-11-25 12:11 | 45986.5076 | 0.0043952 | 3.8219e-05 | 1 | 115 | Unplanned | Lightning | Replace Fuses
755 |  | 1055-26 | Waihi Road | Wairoa | Frasertown 3103 | 2025-11-25 15:59 | 45986.666 | 2025-11-25 17:38 | 45986.7347 | 0.030269 | 0.00030575 | 8 | 792 | Unplanned | Lightning | Replaced faulty transformer W669 due to Lightning
756 |  | 3929-26 | Kaiaua Road | Gisborne | Toko Tie 0401 | 2025-11-26 09:05 | 45987.3785 | 2025-11-26 13:45 | 45987.5729 | 0.17122 | 0.0006115 | 16 | 2241.4676 | Planned | Planned | Replace poles
757 |  | 6212-26 | 438 Cricklewood Road | Wairoa | Raupunga 3101 | 2025-11-26 09:50 | 45987.4097 | 2025-11-26 11:54 | 45987.4958 | 0.0094783 | 7.6438e-05 | 2 | 248 | Unplanned | Unknown cause | Replace Fuses
758 |  | 3966-26 | Waingake Road | Gisborne | Te Arai 0906 | 2025-11-27 08:34 | 45988.3569 | 2025-11-27 13:18 | 45988.5542 | 0.054271 | 0.00019109 | 5 | 1420 | Planned | Planned | Cut trees on Private line
759 |  | 3928-26 | Anaura Road | Gisborne | Mata 0304 | 2025-11-27 09:08 | 45988.3806 | 2025-11-27 15:39 | 45988.6521 | 0.17932 | 0.00045863 | 12 | 2347.0759 | Planned | Planned | Replace 11kV poles G1492 & G1493
760 |  | 3950-26 | Matawai Road | Gisborne | Waimata 0903 | 2025-11-27 09:11 | 45988.3826 | 2025-11-27 12:00 | 45988.5 | 0.37462 | 0.0022167 | 58 | 9802 | Planned | Planned | Upgrade TX D4322 to 50kVA 3phase
761 |  | 1056-26 | Moanui Road | Gisborne | Matawai 1204 | 2025-11-27 14:31 | 45988.6049 | 2025-11-29 13:21 | 45990.5563 | 0.83421 | 0.00099369 | 26 | 21827 | Unplanned | Defective Equipment | To replace burnt HV pole F2518
762 |  | 3931-26 | Mangapoike Road | Wairoa | Frasertown 3103 | 2025-11-28 08:33 | 45989.3562 | 2025-11-28 15:20 | 45989.6389 | 1.1044 | 0.0027135 | 71 | 14487.7067 | Planned | Planned | To replace HV pole W6098
763 |  | 6213-26 | 2090 Whangara Road | Gisborne | Dalton 0502 | 2025-11-28 08:35 | 45989.3576 | 2025-11-28 10:30 | 45989.4375 | 0.0087904 | 7.6438e-05 | 2 | 230 | Unplanned | Unknown cause | Replace Fuses
764 |  | 6215-26 | 140 Matanui Road | Gisborne | Tauwhareparae 0404 | 2025-11-28 09:05 | 45989.3785 | 2025-11-28 10:40 | 45989.4444 | 0.0072616 | 7.6438e-05 | 2 | 190 | Unplanned | Wildlife | Replace Fuses
765 |  | 3964-26 | Frasertown Road | Wairoa | Nuhaka 3203 | 2025-11-28 09:34 | 45989.3986 | 2025-11-28 11:11 | 45989.466 | 0.21502 | 0.0022167 | 58 | 5626 | Planned | Planned | Isolated HV line to allow High Load Transportation
766 |  | 6216-26 | 416 Waiomatatine Road | Gisborne | Ruatoria 0201 | 2025-11-28 13:39 | 45989.5687 | 2025-11-28 15:38 | 45989.6514 | 0.059125 | 0.00049685 | 13 | 1547 | Unplanned | Vegetation | Replace Fuses
767 |  | 1047-26 | Ihungia Road | Gisborne | Mata 0304 | 2025-11-28 16:03 | 45989.6687 | 2025-11-28 16:37 | 45989.6924 | 0.0038983 | 0.00011466 | 3 | 102 | Unplanned | Third Party Interference | Carried out shutdown to remove the generator after tree cutting was complete by forestry
768 |  | 6217-26 | 212 Maraehare Road | Gisborne | Tiki Tiki 0206 | 2025-11-29 06:53 | 45990.2868 | 2025-11-29 09:35 | 45990.3993 | 0.012383 | 7.6438e-05 | 2 | 324 | Unplanned | Wildlife | Put an additional Possum guard on TX Pole also
769 |  | 6218-26 | 66 Poroporo Road | Gisborne | Tiki Tiki 0206 | 2025-11-29 07:27 | 45990.3104 | 2025-11-29 09:35 | 45990.3993 | 0.004892 | 3.8219e-05 | 1 | 128 | Unplanned | Wildlife | Replace Fuses
770 |  | 6219-26 | 34 Matairua Road | Gisborne | Mata 0304 | 2025-11-29 08:31 | 45990.3549 | 2025-11-29 11:20 | 45990.4722 | 0.006459 | 3.8219e-05 | 1 | 169 | Unplanned | Adverse Weather | Replace Fuses
771 |  | 6214-26 | 322 Waingake Road | Gisborne | Te Arai 0906 | 2025-11-30 08:01 | 45991.334 | 2025-11-30 08:45 | 45991.3646 | 0.0016816 | 3.8219e-05 | 1 | 44 | Unplanned | Unknown cause | Replace Fuses
772 |  | 6220-26 | 1584 Mangapoike Road | Wairoa | Frasertown 3103 | 2025-12-01 08:56 | 45992.3722 | 2025-12-01 10:43 | 45992.4465 | 0.0040894 | 3.8219e-05 | 1 | 107 | Unplanned | Lightning | Replace Fuses
773 |  | 3932-26 | Panikau Road / Stevens Road | Gisborne | Dalton 0502 | 2025-12-01 09:19 | 45992.3882 | 2025-12-01 14:15 | 45992.5938 | 0.32807 | 0.0011084 | 29 | 4079.016 | Planned | Planned | Replace HV poles
774 |  | 1057-26 | Lottin Point Rd | Gisborne | Hicks Bay 0102 | 2025-12-01 19:08 | 45992.7972 | 2025-12-02 12:40 | 45993.5278 | 0.52475 | 0.00072616 | 19 | 13730 | Unplanned | Defective Equipment | Broken HV conductor between poles J4590 - J4591
775 |  | 6221-26 | 5645 Centennial Marine Drive | Gisborne | JNL_A 1405 | 2025-12-02 06:37 | 45993.2757 | 2025-12-02 07:33 | 45993.3146 | 0.014982 | 0.00026753 | 7 | 392 | Unplanned | Wildlife | Replace Fuses
776 |  | 3941-26 | Otoki Orchard SH2 | Wairoa | Nuhaka 3203 | 2025-12-02 08:42 | 45993.3625 | 2025-12-02 14:17 | 45993.5951 | 0.19205 | 0.00057328 | 15 | 2513.9404 | Planned | Planned | Tree cutting
777 |  | 1058-26 | Bloomfield Road | Gisborne | Bushmere 0805 | 2025-12-02 08:47 | 45993.366 | 2025-12-02 09:55 | 45993.4132 | 0.010396 | 0.00015288 | 4 | 272 | Unplanned | Third Party Interference | Truck contacted O/H 400V & damaged conductor
778 |  | 3940-26 | Muriwai Feeder - SH2 South | Gisborne | Muriwai 0905 | 2025-12-02 09:00 | 45993.375 | 2025-12-02 13:36 | 45993.5667 | 1.7889 | 0.0064972 | 170 | 23511.1674 | Planned | Planned | HV line maintenance
779 |  | 3920-26 | Kopuaroa Road | Gisborne | Inland 0301 | 2025-12-02 09:13 | 45993.384 | 2025-12-02 14:28 | 45993.6028 | 0.15536 | 0.00049685 | 13 | 2033.1874 | Planned | Planned | To replace 11kV poles
780 |  | 3951-26 | Rangitukia | Gisborne | Tiki Tiki 0206 | 2025-12-02 14:00 | 45993.5833 | 2025-12-02 16:43 | 45993.6965 | 0.6915 | 0.0042423 | 111 | 6688.2538 | Planned | Planned | Install new 2phase 30kVA Transformer J2102
781 |  | 1059-26 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-12-03 05:52 | 45994.2444 | 2025-12-03 13:31 | 45994.5632 | 0.11202 | 0.00026753 | 7 | 2931 | Unplanned | Lightning | Replace TX's D174 & D1747
782 |  | 1061-26 | Walker Road | Gisborne | Ruatoria 0201 | 2025-12-03 08:34 | 45994.3569 | 2025-12-05 13:56 | 45996.5806 | 0.28152 | 0.00049685 | 13 | 7366 | Unplanned | Defective Equipment | Pole J1720 broken. Conductor cut away @ Pole J1719. Pole replacement booked for Friday 5/12. One ICP @ TX J122 remains off until pole replaced 5/12
783 |  | 1060-26 | Kaiti | Gisborne | Herschell 0501 | 2025-12-03 08:51 | 45994.3688 | 2025-12-08 22:51 | 45999.9521 | 2.0333 | 0.020065 | 525 | 53200 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
784 |  | 1060-26 | Kaiti | Gisborne | Dalton 0502 | 2025-12-03 08:51 | 45994.3688 | 2025-12-08 22:50 | 45999.9514 | 9.4406 | 0.087751 | 2296 | 247012 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
785 |  | 1060-26 | Kaiti | Gisborne | Tamarau 0503 | 2025-12-03 08:51 | 45994.3688 | 2025-12-08 22:53 | 45999.9535 | 9.9079 | 0.11584 | 3031 | 259241 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
786 |  | 1060-26 | Kaiti | Gisborne | Whangara 0506 | 2025-12-03 08:51 | 45994.3688 | 2025-12-03 18:47 | 45994.7826 | 2.8661 | 0.051901 | 1358 | 74991 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
787 |  | 1060-26 | Kaiti | Gisborne | Wainui 0504 | 2025-12-03 08:51 | 45994.3688 | 2025-12-08 21:58 | 45999.9153 | 2.8502 | 0.060768 | 1590 | 74576 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
788 |  | 1060-26 | Kaiti | Gisborne | Kaiti LS 0520 | 2025-12-03 08:51 | 45994.3688 | 2025-12-10 14:06 | 46001.5875 | 0.016434 | 0.00019109 | 5 | 430 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
789 |  | 1062-26 | Wainui Road | Gisborne | Tamarau 0503 | 2025-12-03 13:13 | 45994.5507 | 2025-12-03 14:16 | 45994.5944 | 0.26486 | 0.0042041 | 110 | 6930 | Unplanned | Lightning | To repair open HV jumper at pole A2324
790 |  | 1063-26 | Richardson Road | Gisborne | Tiniroto 1003 | 2025-12-03 13:15 | 45994.5521 | 2025-12-03 19:14 | 45994.8014 | 0.052666 | 0.00026753 | 7 | 1378 | Unplanned | Lightning | Lightning strike damaged TX D293, TX replaced
791 |  | 1064-26 | Tuakau Rd, Ihungia Rd | Gisborne | Mata 0304 | 2025-12-03 15:25 | 45994.6424 | 2025-12-04 13:54 | 45995.5792 | 0.093331 | 0.00076438 | 20 | 2442 | Unplanned | Defective Equipment | Broken conductor at pole H1247. Jumpers cut either side of break to restore power until repair was made the next day
792 |  | 1060-26 | Kaiti | Gisborne | Crawford 1504 | 2025-12-03 17:08 | 45994.7139 | 2025-12-09 00:54 | 46000.0375 | 8.6491 | 0.18028 | 4717 | 226303 | Unplanned | Defective Equipment | Transformer at Kaiti substation tripped due to flashover of 11kV Switchgear CB516
793 |  | 1065-26 | Patutahi Substation | Gisborne | Patutahi LS 0920 | 2025-12-03 20:42 | 45994.8625 | 2025-12-03 20:47 | 45994.866 | 0.00019109 | 3.8219e-05 | 1 | 5 | Unplanned | Lightning | Lightning strike on Makaraka - Patutahi 50kV line
794 |  | 1065-26 | Patutahi Substation | Gisborne | Te Arai 0906 | 2025-12-03 20:42 | 45994.8625 | 2025-12-03 20:47 | 45994.866 | 0.045098 | 0.0090197 | 236 | 1180 | Unplanned | Lightning | Lightning strike on Makaraka - Patutahi 50kV line
795 |  | 1065-26 | Patutahi Substation | Gisborne | Lavenham 0902 | 2025-12-03 20:42 | 45994.8625 | 2025-12-03 20:48 | 45994.8667 | 0.10594 | 0.017657 | 462 | 2772 | Unplanned | Lightning | Lightning strike on Makaraka - Patutahi 50kV line
796 |  | 1065-26 | Patutahi Substation | Gisborne | Waimata 0903 | 2025-12-03 20:42 | 45994.8625 | 2025-12-03 20:48 | 45994.8667 | 0.14997 | 0.024995 | 654 | 3924 | Unplanned | Lightning | Lightning strike on Makaraka - Patutahi 50kV line
797 |  | 1065-26 | Patutahi Substation | Gisborne | Muriwai 0905 | 2025-12-03 20:42 | 45994.8625 | 2025-12-03 20:48 | 45994.8667 | 0.096541 | 0.01609 | 421 | 2526 | Unplanned | Lightning | Lightning strike on Makaraka - Patutahi 50kV line
798 |  | 6222-26 | 106 Papatu Road | Gisborne | Muriwai 0905 | 2025-12-03 20:50 | 45994.8681 | 2025-12-04 12:53 | 45995.5368 | 1.0673 | 0.0011084 | 29 | 27927 | Unplanned | Lightning | Also blown fuses C607, C1346, C606, C605
799 |  | 1066-26 | Mahia East: Pongaroa, Kinikini, Onenui | Wairoa | Mahia 3301 | 2025-12-04 04:29 | 45995.1868 | 2025-12-04 21:18 | 45995.8875 | 1.472 | 0.0043952 | 115 | 38516 | Unplanned | Lightning | Lightning strikes. Repairs needed at W943, W8991 & W306
800 |  | 6238-26 | 686 Okare Road | Wairoa | Ruakituri 2003 | 2025-12-04 05:18 | 45995.2208 | 2025-12-04 11:30 | 45995.4792 | 0.028435 | 7.6438e-05 | 2 | 744 | Unplanned | Lightning | Replace Fuses
801 |  | 6241-26 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2025-12-04 06:08 | 45995.2556 | 2025-12-04 14:51 | 45995.6188 | 0.15991 | 0.00030575 | 8 | 4184 | Unplanned | Adverse Weather | Replace Fuses
802 |  | 6224-26 | 23 O'Grady road | Gisborne | Bushmere 0805 | 2025-12-04 06:18 | 45995.2625 | 2025-12-04 14:30 | 45995.6042 | 0.094019 | 0.00019109 | 5 | 2460 | Unplanned | Lightning | Replace Fuses
803 |  | 6223-26 | 3350 Lake Road | Wairoa | Frasertown 3103 | 2025-12-04 06:29 | 45995.2701 | 2025-12-04 13:00 | 45995.5417 | 0.014944 | 3.8219e-05 | 1 | 391 | Unplanned | Lightning | Replace Fuses
804 |  | 6225-26 | 921 Ngakaroa Road | Gisborne | Waimata 0903 | 2025-12-04 06:37 | 45995.2757 | 2025-12-04 11:25 | 45995.4757 | 0.022014 | 7.6438e-05 | 2 | 576 | Unplanned | Lightning | Replace Fuses
805 |  | 6226-26 | 114 Opou Road | Gisborne | Muriwai 0905 | 2025-12-04 06:40 | 45995.2778 | 2025-12-04 09:10 | 45995.3819 | 0.063061 | 0.00042041 | 11 | 1650 | Unplanned | Lightning | Replace Fuses
806 |  | 6230-26 | 77 O'Grady road | Gisborne | Bushmere 0805 | 2025-12-04 06:41 | 45995.2785 | 2025-12-04 14:30 | 45995.6042 | 0.035849 | 7.6438e-05 | 2 | 938 | Unplanned | Lightning | Replace Fuses
807 |  | 6228-26 | 413 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2025-12-04 06:44 | 45995.2806 | 2025-12-04 08:30 | 45995.3542 | 0.0040512 | 3.8219e-05 | 1 | 106 | Unplanned | Lightning | Replace Fuses
808 |  | 6227-26 | 155 Gaddums Hill Road | Gisborne | Whangara 0506 | 2025-12-04 06:48 | 45995.2833 | 2025-12-04 08:30 | 45995.3542 | 0.09356 | 0.00091726 | 24 | 2448 | Unplanned | Adverse Weather | Replace Fuses
809 |  | 6229-26 | 1114 Taumata Road | Gisborne | Tahora 1103 | 2025-12-04 06:51 | 45995.2854 | 2025-12-04 18:00 | 45995.75 | 0.025569 | 3.8219e-05 | 1 | 669 | Unplanned | Lightning | Replace Fuses
810 |  | 6231-26 | 386 Matawai Road | Gisborne | Bushmere 0805 | 2025-12-04 06:52 | 45995.2861 | 2025-12-04 12:30 | 45995.5208 | 0.090426 | 0.00026753 | 7 | 2366 | Unplanned | Lightning | Replace Fuses
811 |  | 1072-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-12-04 07:00 | 45995.2917 | 2025-12-05 10:58 | 45996.4569 | 0.12826 | 7.6438e-05 | 2 | 3356 | Unplanned | Lightning | To replace faulty transformer F259 due to lightning
812 |  | 1070-26 | Papatu Road | Gisborne | Muriwai 0905 | 2025-12-04 07:03 | 45995.2937 | 2025-12-04 16:04 | 45995.6694 | 0.32444 | 0.0011084 | 29 | 8489 | Unplanned | Lightning | Transformer C605 damaged in lightning strike, replaced
813 |  | 6232-26 | Toko Radio Site, Maungaaroa Hill | Gisborne | Mata 0304 | 2025-12-04 07:50 | 45995.3264 | 2025-12-04 09:36 | 45995.4 | 0.012154 | 0.00011466 | 3 | 318 | Unplanned | Lightning | Replace Fuses
814 |  | 6233-26 | 1262 Ohuka Road | Wairoa | Ruakituri 2003 | 2025-12-04 08:16 | 45995.3444 | 2025-12-04 11:16 | 45995.4694 | 0.17199 | 0.00095547 | 25 | 4500 | Unplanned | Lightning | Replace Fuses
815 |  | 1067-26 | Mahia, Morere | Wairoa | Morere 3401 | 2025-12-04 08:26 | 45995.3514 | 2025-12-04 09:47 | 45995.4076 | 0.57948 | 0.020333 | 532 | 15162 | Unplanned | Defective Equipment | Conductor down from poles W807 - W951
816 |  | 1067-26 | Mahia, Morere | Wairoa | Mahia 3301 | 2025-12-04 08:26 | 45995.3514 | 2025-12-04 14:19 | 45995.5965 | 1.5445 | 0.034512 | 903 | 40411 | Unplanned | Defective Equipment | Conductor down from poles W807 - W951
817 |  | 3953-26 | Back Ormond road | Gisborne | Haisman 0804 | 2025-12-04 08:35 | 45995.3576 | 2025-12-04 14:38 | 45995.6097 | 2.0533 | 0.0056564 | 148 | 53724 | Planned | Planned | To replace 11kV pole C654 and remove existing stay from pole C1372
818 |  | 6234-26 | 407A Matawai Road | Gisborne | Bushmere 0805 | 2025-12-04 08:38 | 45995.3597 | 2025-12-04 11:30 | 45995.4792 | 0.019721 | 0.00011466 | 3 | 516 | Unplanned | Lightning | Replace Fuses
819 |  | 6235-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2025-12-04 08:54 | 45995.3708 | 2025-12-04 22:51 | 45995.9521 | 0.22393 | 0.00026753 | 7 | 5859 | Unplanned | Unknown cause | Replace Fuses
820 |  | 6242-26 | 2733 Lake Road | Wairoa | Frasertown 3103 | 2025-12-04 09:20 | 45995.3889 | 2025-12-04 14:10 | 45995.5903 | 0.044334 | 0.00015288 | 4 | 1160 | Unplanned | Lightning | Replace Fuses
821 |  | 6236-26 | 91 Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-12-04 09:56 | 45995.4139 | 2025-12-04 11:14 | 45995.4681 | 0.0029811 | 3.8219e-05 | 1 | 78 | Unplanned | Lightning | Replace Fuses
822 |  | 3939-26 | Te Araroa Road | Gisborne | Hicks Bay 0102 | 2025-12-04 10:04 | 45995.4194 | 2025-12-04 13:00 | 45995.5417 | 0.013453 | 7.6438e-05 | 2 | 176.0135 | Planned | Planned | Upgrade TX J369 to 50kVA
823 |  | 6237-26 | 2317 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-12-04 11:00 | 45995.4583 | 2025-12-04 22:00 | 45995.9167 | 0.17657 | 0.00026753 | 7 | 4620 | Unplanned | Lightning | Replace Fuses
824 |  | 1068-26 | Willows Road | Gisborne | Bell 1406 | 2025-12-04 11:09 | 45995.4646 | 2025-12-05 17:23 | 45996.7243 | 0.055265 | 0.00022931 | 6 | 1446 | Unplanned | Defective Equipment | Cable fault beyond HV fuses C3927
825 |  | 6239-26 | Parikanapa Road | Gisborne | Parikanapa 1002 | 2025-12-04 12:05 | 45995.5035 | 2025-12-04 16:00 | 45995.6667 | 0.0089815 | 3.8219e-05 | 1 | 235 | Unplanned | Lightning | Replace Fuses
826 |  | 1069-26 | Makaraka Substation | Gisborne | Campion 0802 | 2025-12-04 12:19 | 45995.5132 | 2025-12-04 13:36 | 45995.5667 | 1.6427 | 0.056488 | 1478 | 42980 | Unplanned | Defective Equipment | 50kV CB32 & CB94 tripped and L/out due to PRD operated at Makaraka Sub
827 |  | 1069-26 | Makaraka Substation | Gisborne | Nelson 0803 | 2025-12-04 12:19 | 45995.5132 | 2025-12-04 13:24 | 45995.5583 | 2.9592 | 0.093942 | 2458 | 77427 | Unplanned | Defective Equipment | 50kV CB32 & CB94 tripped and L/out due to PRD operated at Makaraka Sub
828 |  | 1069-26 | Makaraka Substation | Gisborne | Haisman 0804 | 2025-12-04 12:19 | 45995.5132 | 2025-12-04 13:25 | 45995.559 | 1.3293 | 0.020141 | 527 | 34782 | Unplanned | Defective Equipment | 50kV CB32 & CB94 tripped and L/out due to PRD operated at Makaraka Sub
829 |  | 1069-26 | Makaraka Substation | Gisborne | Bushmere 0805 | 2025-12-04 12:19 | 45995.5132 | 2025-12-04 13:25 | 45995.559 | 0.46161 | 0.0069941 | 183 | 12078 | Unplanned | Defective Equipment | 50kV CB32 & CB94 tripped and L/out due to PRD operated at Makaraka Sub
830 |  | 1069-26 | Makaraka Substation | Gisborne | Makaraka LS 0820 | 2025-12-04 12:19 | 45995.5132 | 2025-12-04 13:22 | 45995.5569 | 0.0022549 | 7.6438e-05 | 2 | 59 | Unplanned | Defective Equipment | 50kV CB32 & CB94 tripped and L/out due to PRD operated at Makaraka Sub
831 |  | 1071-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-12-04 13:20 | 45995.5556 | 2025-12-04 17:04 | 45995.7111 | 0.69956 | 0.003134 | 82 | 18304 | Unplanned | Adverse Weather | Windy conditions, suspect line clash
832 |  | 6240-26 | 218 Mangamaia Road | Gisborne | Whatatutu 1201 | 2025-12-04 14:30 | 45995.6042 | 2025-12-04 20:40 | 45995.8611 | 0.35353 | 0.00095547 | 25 | 9250 | Unplanned | Lightning | Replace Fuses
833 |  | 1074-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-12-04 16:07 | 45995.6715 | 2025-12-05 16:58 | 45996.7069 | 0.22794 | 0.00015288 | 4 | 5964 | Unplanned | Lightning | Transformer F2149 damaged due to lightning strike - replaced
834 |  | 1075-26 | Te Wera Road | Gisborne | Matawai 1204 | 2025-12-04 16:07 | 45995.6715 | 2025-12-05 15:13 | 45996.634 | 0.052972 | 3.8219e-05 | 1 | 1386 | Unplanned | Lightning | Lightning damaged TX F2165, TX replaced
835 |  | 6243-26 | 101 Russell Road | Gisborne | Ngatapa 1102 | 2025-12-05 06:29 | 45996.2701 | 2025-12-05 08:45 | 45996.3646 | 0.057176 | 0.00042041 | 11 | 1496 | Unplanned | Unknown cause | Replace Fuses
836 |  | 6244-26 | 36 Glenroy Road | Gisborne | Dalton 0502 | 2025-12-05 06:43 | 45996.2799 | 2025-12-05 13:48 | 45996.575 | 0.16243 | 0.00038219 | 10 | 4250 | Unplanned | Lightning | Replace Fuses
837 |  | 6245-26 | 758 Glenroy Road | Gisborne | Dalton 0502 | 2025-12-05 07:31 | 45996.3132 | 2025-12-05 15:55 | 45996.6632 | 0.019262 | 3.8219e-05 | 1 | 504 | Unplanned | Unknown cause | Replace Fuses
838 |  | 6246-26 | 353 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-12-05 08:04 | 45996.3361 | 2025-12-05 15:20 | 45996.6389 | 0.033327 | 7.6438e-05 | 2 | 872 | Unplanned | Lightning | Replace Fuses
839 |  | 6248-26 | 353 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2025-12-05 08:04 | 45996.3361 | 2025-12-05 15:20 | 45996.6389 | 0.033327 | 7.6438e-05 | 2 | 872 | Unplanned | Lightning | Fuse wired incorrectly
840 |  | 6249-26 | 485 Taurau Valley Road | Gisborne | Te Arai 0906 | 2025-12-05 08:45 | 45996.3646 | 2025-12-05 14:20 | 45996.5972 | 0.025607 | 7.6438e-05 | 2 | 670 | Unplanned | Lightning | Replace Fuses
841 |  | 3921-26 | Kopuaroa Road | Gisborne | Inland 0301 | 2025-12-05 09:11 | 45996.3826 | 2025-12-05 12:32 | 45996.5222 | 0.094516 | 0.00049685 | 13 | 2473 | Planned | Planned | To Replace 11kV poles
842 |  | 6250-26 | 200 Faulkner Road | Gisborne | Tahora 1103 | 2025-12-05 10:03 | 45996.4187 | 2025-12-05 13:15 | 45996.5521 | 0.022014 | 0.00011466 | 3 | 576 | Unplanned | Lightning | Replace Fuses
843 |  | 3981-26 | Waiomatatini Road, Walker Road | Gisborne | Tiki Tiki 0206 | 2025-12-05 12:40 | 45996.5278 | 2025-12-05 13:56 | 45996.5806 | 0.040665 | 0.00053507 | 14 | 1064 | Planned | Planned | Replace pole J1720
844 |  | 6247-26 | 2789 Tiniroto Road | Gisborne | Tiniroto 1003 | 2025-12-05 18:31 | 45996.7715 | 2025-12-05 19:39 | 45996.8187 | 0.0025989 | 3.8219e-05 | 1 | 68 | Unplanned | Lightning | Replace Fuses
845 |  | 6253-26 | 156 Te Wera Road | Gisborne | Matawai 1204 | 2025-12-06 09:13 | 45997.384 | 2025-12-06 19:54 | 45997.8292 | 0.024498 | 3.8219e-05 | 1 | 641 | Unplanned | Unknown cause | Replace Fuses
846 |  | 1076-26 | Willows Feeder | Gisborne | Willows 0702 | 2025-12-06 12:09 | 45997.5062 | 2025-12-10 11:04 | 46001.4611 | 0.16648 | 0.0034779 | 91 | 4356 | Unplanned | Defective Equipment | Blown cable termination at pole B6310
847 |  | 6251-26 | 338 Tuahu Road | Gisborne | Tauwhareparae 0404 | 2025-12-06 14:07 | 45997.5882 | 2025-12-06 21:15 | 45997.8854 | 0.016358 | 3.8219e-05 | 1 | 428 | Unplanned | Lightning | Replace Fuses
848 |  | 6252-26 | 111 Richardson Road | Gisborne | Tiniroto 1003 | 2025-12-06 15:04 | 45997.6278 | 2025-12-06 19:51 | 45997.8271 | 0.076782 | 0.00026753 | 7 | 2009 | Unplanned | Unknown cause | Whole of Richardson Road power was restored
849 |  | 1077-26 | Mata Feeder beyond H360 | Gisborne | Mata 0304 | 2025-12-06 15:58 | 45997.6653 | 2025-12-06 17:37 | 45997.734 | 0.32918 | 0.0033251 | 87 | 8613 | Unplanned | Third Party Interference | De-energise HV on Mata feeder beyond H360 at request of FENZ, fire on Waiapu Road requires helicopter water drop
850 |  | 1078-26 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2025-12-06 17:58 | 45997.7486 | 2025-12-07 13:16 | 45998.5528 | 0.31898 | 0.0017963 | 47 | 8346 | Unplanned | Lightning | Replace faulty transformer - Suspect lightning
851 |  | 6254-26 | 590 Tuparoa Road | Gisborne | Ruatoria 0201 | 2025-12-07 09:50 | 45998.4097 | 2025-12-07 19:01 | 45998.7924 | 0.021059 | 3.8219e-05 | 1 | 551 | Unplanned | Unknown cause | Replace Fuses
852 |  | 6255-26 | 55 Tapuihikitia Road | Gisborne | Whatatutu 1201 | 2025-12-08 07:34 | 45999.3153 | 2025-12-08 11:22 | 45999.4736 | 0.095853 | 0.00042041 | 11 | 2508 | Unplanned | Wildlife | Replace Fuses
853 |  | 1079-26 | Mohaka, Raupunga, Paroa | Wairoa | Raupunga 3101 | 2025-12-08 15:48 | 45999.6583 | 2025-12-11 14:53 | 46002.6201 | 2.4888 | 0.013415 | 351 | 65120 | Unplanned | Third Party Interference | Supply disconnected for safety reasons after reports of fire under power line near Te Kumi Road, Mohaka. Fire betwn poles W6428 - W6425. Two poles burnt in fire and require replacement. W6426 & W6426
854 |  | 1080-26 | Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2025-12-08 19:23 | 45999.8076 | 2025-12-08 20:06 | 45999.8375 | 0.042729 | 0.00099369 | 26 | 1118 | Unplanned | Defective Equipment | LI reported wire off insulator
855 |  | 1081-26 | Campion Feeder | Gisborne | Campion 0802 | 2025-12-08 20:11 | 45999.841 | 2025-12-08 22:13 | 45999.9257 | 1.6661 | 0.028244 | 739 | 43594 | Unplanned | Defective Equipment | Cable fault at Ring Main Switch C731
856 |  | 3937-26 | Riverside Road | Gisborne | Waimata 0903 | 2025-12-09 08:38 | 46000.3597 | 2025-12-09 16:15 | 46000.6771 | 0.33186 | 0.00072616 | 19 | 4202.0491 | Planned | Planned | To replace 11kV poles
857 |  | 1082A-26 | Kahutia | Gisborne | Kahutia 0601 | 2025-12-09 11:12 | 46000.4667 | 2025-12-10 18:51 | 46001.7854 | 0.12945 | 0.0008026 | 21 | 3387 | Unplanned | Defective Equipment | Blown HV cable termination at Ring Main Switch B1096
858 |  | 1085-26 | Ngatapa | Gisborne | Ngatapa 1102 | 2025-12-10 06:56 | 46001.2889 | 2025-12-10 12:40 | 46001.5278 | 0.4237 | 0.0043187 | 113 | 11086 | Unplanned | Vegetation | Tree fell on Pole/Lines
859 |  | 3942-26 | Whakarau Road | Gisborne | Matawai 1204 | 2025-12-10 08:38 | 46001.3597 | 2025-12-10 14:29 | 46001.6035 | 0.24147 | 0.00068794 | 18 | 3161.1732 | Planned | Planned | To replace 11kV poles
860 |  | 1086-26 | Waiomatatini Road | Gisborne | Tiki Tiki 0206 | 2025-12-10 11:59 | 46001.4993 | 2025-12-10 13:18 | 46001.5542 | 0.030193 | 0.00038219 | 10 | 790 | Unplanned | Defective Equipment | Replace pole J966, pole had broken but conductor was intact
861 |  | 6256-26 | 450 Ngamotu Road | Wairoa | Affco 3202 | 2025-12-10 17:31 | 46001.7299 | 2025-12-10 18:33 | 46001.7729 | 0.0071087 | 0.00011466 | 3 | 186 | Unplanned | Defective Equipment | Replace Fuses
862 |  | 1087-26 | Mahia | Wairoa | Mahia 3301 | 2025-12-11 06:20 | 46002.2639 | 2025-12-11 07:02 | 46002.2931 | 1.135 | 0.035888 | 939 | 29696 | Unplanned | Defective Equipment | Pole W3763 conductor down and pole on fire
863 |  | 1087-26 | Mahia | Wairoa | Morere 3401 | 2025-12-11 06:20 | 46002.2639 | 2025-12-11 06:57 | 46002.2896 | 0.24147 | 0.010166 | 266 | 6318 | Unplanned | Defective Equipment | Pole W3763 conductor down and pole on fire
864 |  | 3002-26 | Herschell | Gisborne | Herschell 0501 | 2025-12-11 09:01 | 46002.3757 | 2025-12-11 13:45 | 46002.5729 | 1.9212 | 0.0067648 | 177 | 50268 | Planned | Planned | Inspection and cleaning of Bus 1
865 |  | 6257-26 | 1048 Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2025-12-11 17:41 | 46002.7368 | 2025-12-11 21:05 | 46002.8785 | 0.0077967 | 3.8219e-05 | 1 | 204 | Unplanned | Lightning | Apparently been bad boltages since lightning last Wednesday. Check TX, buzzing like crazy when LV fuses removed. Pulled HV. Walk up hill to 2 x H Poles J2950 & J2951. Ok. Test voltage along road and multiple places with proximity tester. Found new H Pole J2703 had two blown fuses. Not aware of new fuses
866 |  | 3003-26 | De Latour Rd, Owen Rd, Martin Rd, Turenne St | Gisborne | Crawford 1504 | 2025-12-11 17:42 | 46002.7375 | 2025-12-11 18:24 | 46002.7667 | 0.55058 | 0.013109 | 343 | 14406 | Planned | Planned | To reconnect HV jumpers at pole A6458
867 |  | 6258-26 | 3350 Lake Road | Wairoa | Frasertown 3103 | 2025-12-11 19:55 | 46002.8299 | 2025-12-11 21:33 | 46002.8979 | 0.0037455 | 3.8219e-05 | 1 | 98 | Unplanned | Lightning | Replace Fuses
868 |  | 3943-26 | Whakarau Road | Gisborne | Matawai 1204 | 2025-12-12 08:31 | 46003.3549 | 2025-12-12 14:28 | 46003.6028 | 0.2456 | 0.00068794 | 18 | 3215.2104 | Planned | Planned | To replace 11kV poles
869 |  | 3938-26 | Riverside Road | Gisborne | Waimata 0903 | 2025-12-12 08:35 | 46003.3576 | 2025-12-12 11:41 | 46003.4868 | 0.063979 | 0.00034397 | 9 | 1674 | Planned | Planned | To replace 11kV Poles
870 |  | 3952-26 | Waihau Road | Gisborne | Rototahi 0403 | 2025-12-12 09:00 | 46003.375 | 2025-12-12 14:38 | 46003.6097 | 0.038754 | 0.00011466 | 3 | 507.0619 | Planned | Planned | Replace pole and transformer A259
871 |  | 1088-26 | Waikura Road | Gisborne | Hicks Bay 0102 | 2025-12-12 12:45 | 46003.5312 | 2025-12-13 14:03 | 46004.5854 | 0.81418 | 0.0018727 | 49 | 21303 | Unplanned | Third Party Interference | Broken conductor between J4635-J4636 & cracked insulators at pole J4638 due to vehicle crashing into pole
872 |  | 1089-26 | Centennial Crescent | Gisborne | Elgin 0703 | 2025-12-13 03:30 | 46004.1458 | 2025-12-13 15:43 | 46004.6549 | 1.961 | 0.0026753 | 70 | 51310 | Unplanned | Third Party Interference | Transformer hit by vehicle, replaced
873 |  | 3978-26 | Parkinson Street | Gisborne | Solander 0706 | 2025-12-13 08:10 | 46004.3403 | 2025-12-13 13:03 | 46004.5437 | 0.0071087 | 3.8219e-05 | 1 | 186 | Planned | Planned | Transformer termination checks carries out at customers request
874 |  | 3008A-26 | Bright St, Peel St, Kahutia St | Gisborne | Reads Quay 0603 | 2025-12-14 10:01 | 46005.4174 | 2025-12-14 14:26 | 46005.6014 | 0.21269 | 0.0008026 | 21 | 5565 | Planned | Planned | Replenish oil in Ring Main Units
875 |  | 6259-26 | 3286 Lake Road | Wairoa | Frasertown 3103 | 2025-12-14 11:41 | 46005.4868 | 2025-12-14 12:47 | 46005.5326 | 0.0025225 | 3.8219e-05 | 1 | 66 | Unplanned | Lightning | Replace Fuses
876 |  | 6260-26 | 682 Titirangi Road | Wairoa | Frasertown 3103 | 2025-12-15 08:10 | 46006.3403 | 2025-12-15 12:42 | 46006.5292 | 0.020791 | 7.6438e-05 | 2 | 544 | Unplanned | Lightning | Replace Fuses
877 |  | 6262-26 | 682 Titirangi Road | Wairoa | Frasertown 3103 | 2025-12-15 08:10 | 46006.3403 | 2025-12-15 12:42 | 46006.5292 | 0.020791 | 7.6438e-05 | 2 | 544 | Unplanned | Lightning | Replace Fuses
878 |  | 3991-26 | Mangatu road | Gisborne | Whatatutu 1201 | 2025-12-15 08:31 | 46006.3549 | 2025-12-15 13:29 | 46006.5618 | 0.29612 | 0.00099369 | 26 | 7748 | Planned | Planned | To clear bamboo at pole E168
879 |  | 1092-26 | Gordon Road | Gisborne | Te Arai 0906 | 2025-12-15 09:40 | 46006.4028 | 2025-12-16 10:37 | 46007.4424 | 0.057214 | 3.8219e-05 | 1 | 1497 | Unplanned | Lightning | To replace faulty transformer C5859
880 |  | 3977-26 | Blakes Approach | Wairoa | Mahia 3301 | 2025-12-15 10:09 | 46006.4229 | 2025-12-15 13:04 | 46006.5444 | 0.5752 | 0.0032868 | 86 | 7549.7334 | Planned | Planned | To install HV cable @ pole W9875
881 |  | 6261-26 | 1175 Waiapu Road | Gisborne | Toko Tie 0401 | 2025-12-15 15:02 | 46006.6264 | 2025-12-15 15:34 | 46006.6486 | 0.003669 | 0.00011466 | 3 | 96 | Unplanned | Vegetation | URGENT tree cutting
882 |  | 6263-26 | 673F Riverside road | Gisborne | Whangara 0506 | 2025-12-16 07:22 | 46007.3069 | 2025-12-16 09:00 | 46007.375 | 0.044946 | 0.00045863 | 12 | 1176 | Unplanned | Unknown cause | Livened and held in
883 |  | 3983-26 | Back Ormond road | Gisborne | Haisman 0804 | 2025-12-16 08:32 | 46007.3556 | 2025-12-16 15:31 | 46007.6465 | 2.37 | 0.0056564 | 148 | 62012 | Planned | Planned | Install new 50kV Pole
884 |  | 3968-26 | Lavenham Road | Gisborne | Lavenham 0902 | 2025-12-16 08:33 | 46007.3562 | 2025-12-16 16:39 | 46007.6937 | 1.3374 | 0.0027518 | 72 | 17544.1449 | Planned | Planned | To carry out maintenance TX D577 & D384
885 |  | 1093-26 | Willow Flat Road | Wairoa | Raupunga 3101 | 2025-12-16 09:06 | 46007.3792 | 2025-12-16 12:17 | 46007.5118 | 0.036499 | 0.00019109 | 5 | 955 | Unplanned | Defective Equipment | To resag low HV conductor at pole W5230
886 |  | 1095-26 | Wharekopae Road | Gisborne | Lavenham 0902 | 2025-12-16 20:54 | 46007.8708 | 2025-12-17 13:49 | 46008.5757 | 0.72108 | 0.020256 | 530 | 18867 | Unplanned | Third Party Interference | To replace broken TX pole D342 caused by vehicle accident
887 |  | 1097-26 | Raupunga | Wairoa | Raupunga 3101 | 2025-12-17 06:34 | 46008.2736 | 2025-12-18 15:42 | 46009.6542 | 1.1731 | 0.0098605 | 258 | 30694 | Unplanned | Vegetation | Tree through the lines beyond pole W5551
888 |  | 3969-26 | Tiniroto Road | Gisborne | Lavenham 0902 | 2025-12-17 08:34 | 46008.3569 | 2025-12-17 13:24 | 46008.5583 | 0.28817 | 0.00099369 | 26 | 3773.7462 | Planned | Planned | To carry out maintenance
889 |  | 3004-26 | Armstrong Road | Gisborne | Whatatutu 1201 | 2025-12-17 09:01 | 46008.3757 | 2025-12-17 15:35 | 46008.6493 | 0.12047 | 0.00030575 | 8 | 3152 | Planned | Planned | Isolate for tree clearance
890 |  | 1098-26 | East Cape Road | Gisborne | Te Araroa 0103 | 2025-12-17 09:20 | 46008.3889 | 2025-12-18 12:57 | 46009.5396 | 0.66325 | 0.0014905 | 39 | 17354 | Unplanned | Defective Equipment | To replace burnt HV pole J3760
891 |  | 1099-26 | Waimata Valley Road | Gisborne | Waimata 0903 | 2025-12-17 13:17 | 46008.5535 | 2025-12-17 16:12 | 46008.675 | 0.018154 | 0.00038219 | 10 | 475 | Unplanned | Third Party Interference | To Repair broken LV conductor between poles G206 - G207
892 |  | 3979-26 | Tiniroto Road | Gisborne | Muriwai 0905 | 2025-12-18 08:30 | 46009.3542 | 2025-12-18 11:58 | 46009.4986 | 0.19079 | 0.00091726 | 24 | 2498.3115 | Planned | Planned | To replace TX C163
893 |  | 6264-26 | 240 Rockhill road | Gisborne | W O Kuri 1001 | 2025-12-18 09:27 | 46009.3938 | 2025-12-18 22:00 | 46009.9167 | 0.086337 | 0.00011466 | 3 | 2259 | Unplanned | Adverse Weather | Blown DDO's replaced 5a fuses
894 |  | 6265-26 | 146 Makaretu Road | Gisborne | Matawai 1204 | 2025-12-18 13:08 | 46009.5472 | 2025-12-18 15:30 | 46009.6458 | 0.032563 | 0.00022931 | 6 | 852 | Unplanned | Lightning | Lightening strikes, blew line isolation fuses
895 |  | 6266-26 | 157 Matakaoa Road | Gisborne | Hicks Bay 0102 | 2025-12-18 18:31 | 46009.7715 | 2025-12-18 20:58 | 46009.8736 | 0.10675 | 0.00072616 | 19 | 2793 | Unplanned | Unknown cause | Replace Fuses
896 |  | 3980-26 | Bloomfield Road | Gisborne | Bell 1406 | 2025-12-19 08:03 | 46010.3354 | 2025-12-19 12:03 | 46010.5021 | 0.13759 | 0.00057328 | 15 | 1801.0319 | Planned | Planned | Replace TX Structure C109
897 |  | 6267-26 | 1031 Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2025-12-21 10:06 | 46012.4208 | 2025-12-21 13:26 | 46012.5597 | 0.0076438 | 3.8219e-05 | 1 | 200 | Unplanned | Unknown cause | Replace Fuses
898 |  | 1096-26 | 6272 Waiapu Road | Gisborne | Makarika 0204 | 2025-12-22 15:06 | 46013.6292 | 2025-12-22 16:00 | 46013.6667 | 0.0020638 | 3.8219e-05 | 1 | 54 | Unplanned | Third Party Interference | Outage to upgrade TX H69 from 1ph to 2phase. Customer initiated
899 |  | 6268-26 | 65 Tapuihikitia Road | Gisborne | Whatatutu 1201 | 2025-12-23 06:35 | 46014.2743 | 2025-12-23 08:55 | 46014.3715 | 0.042805 | 0.00030575 | 8 | 1120 | Unplanned | Vegetation | Restored power to Tapuihikitia Road. Fault beyond HV fuses F4811
900 |  | 1101-26 | Mangaone Valley Road | Wairoa | Morere 3401 | 2025-12-23 14:20 | 46014.5972 | 2025-12-23 18:31 | 46014.7715 | 0.2323 | 0.0032486 | 85 | 6078 | Unplanned | Third Party Interference | Farm excavator brought down lines @ pole W8075
901 |  | 6269-26 | 132 & 78 Tansley Road | Gisborne | Lavenham 0902 | 2025-12-23 14:24 | 46014.6 | 2025-12-23 17:15 | 46014.7188 | 0.065354 | 0.00038219 | 10 | 1710 | Unplanned | Unknown cause | Replace Fuses
902 |  | 6270-26 | 198 Ormond Valley Road | Gisborne | Waimata 0903 | 2025-12-23 16:55 | 46014.7049 | 2025-12-23 19:57 | 46014.8313 | 0.034779 | 0.00019109 | 5 | 910 | Unplanned | Vegetation | Trees need to be removed
903 |  | 1102-26 | Esplanade | Gisborne | Esplanade 1503 | 2025-12-23 17:38 | 46014.7347 | 2025-12-23 20:38 | 46014.8597 | 2.3135 | 0.050526 | 1322 | 60533 | Unplanned | Defective Equipment | To repair blown underground 11kV cable betwn Ring main switch A194-B459
904 |  | 6271-26 | 599 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2025-12-23 18:05 | 46014.7535 | 2025-12-23 19:20 | 46014.8056 | 0.025798 | 0.00034397 | 9 | 675 | Unplanned | Adverse Weather | Replace Fuses
905 |  | 1102-26 | Esplanade | Gisborne | Harris 1502 | 2025-12-23 19:06 | 46014.7958 | 2025-12-23 19:09 | 46014.7979 | 0.097458 | 0.032486 | 850 | 2550 | Unplanned | Defective Equipment | To repair blown underground 11kV cable betwn Ring main switch A194-B459
906 |  | 1103-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2025-12-23 23:12 | 46014.9667 | 2025-12-24 13:24 | 46015.5583 | 1.8235 | 0.0021403 | 56 | 47712 | Unplanned | Vegetation | Tree through HV @ D5040 - D5041. Tree burning in HV @ D5071 - D5072
907 |  | 1105-26 | Whangara Road | Gisborne | Rototahi 0403 | 2025-12-24 10:12 | 46015.425 | 2025-12-24 17:44 | 46015.7389 | 0.72028 | 0.0086375 | 226 | 18846 | Unplanned | Vegetation | Vine covering pole A821 caught on fire
908 |  | 6272-26 | 51 Poynter Road | Gisborne | Te Karaka 1203 | 2025-12-24 20:43 | 46015.8632 | 2025-12-24 23:34 | 46015.9819 | 0.07189 | 0.00042041 | 11 | 1881 | Unplanned | Unknown cause | Replace Fuses
909 |  | 1106-26 | Back Ormond Road, Snowsill Road | Gisborne | Waimata 0903 | 2025-12-25 07:59 | 46016.3326 | 2025-12-25 14:18 | 46016.5958 | 0.49853 | 0.0032868 | 86 | 13044 | Unplanned | Third Party Interference | Car V's pole E1880 - Pole held secure overnight
910 |  | 6273-26 | 64 Repongaere Road | Gisborne | Lavenham 0902 | 2025-12-25 21:16 | 46016.8861 | 2025-12-25 22:41 | 46016.9451 | 0.032486 | 0.00038219 | 10 | 850 | Unplanned | Unknown cause | Replace Fuses
911 |  | 1107-26 | Lavenham Rd, Renner Road, Judd Road | Gisborne | Lavenham 0902 | 2025-12-25 23:24 | 46016.975 | 2025-12-26 09:33 | 46017.3979 | 0.96564 | 0.006115 | 160 | 25266 | Unplanned | Vegetation | Tree through HV conductor @ Pole D1983 - D1970
912 |  | 1108-26 | Ngakoroa Road | Gisborne | Waimata 0903 | 2025-12-26 12:26 | 46017.5181 | 2025-12-26 17:05 | 46017.7118 | 0.031989 | 0.00011466 | 3 | 837 | Unplanned | Vegetation | Tree through underbuilt 400V conductor @ Pole E2897 - E2898
913 |  | 1109-26 | Tauwhareparae | Gisborne | Tauwhareparae 0404 | 2025-12-27 09:27 | 46018.3938 | 2025-12-28 11:11 | 46019.466 | 0.25003 | 0.0019109 | 50 | 6542 | Unplanned | Defective Equipment | HV Fuses TX G212 required replacement
914 |  | 6274-26 | 3441 Waitahaia Road | Gisborne | Te Araroa 0103 | 2025-12-28 08:44 | 46019.3639 | 2025-12-28 13:10 | 46019.5486 | 0.25416 | 0.00095547 | 25 | 6650 | Unplanned | Adverse Weather | Replace Fuses
915 |  | 1110-26 | Matawai Rd / Hiriroroa Rd Nth / Makaretu Road | Gisborne | Matawai 1204 | 2025-12-28 16:30 | 46019.6875 | 2025-12-28 18:56 | 46019.7889 | 0.17909 | 0.0019492 | 51 | 4686 | Unplanned | Unknown cause | Line patrolled unable to identfy cause of EF
916 |  | 6275-26 | 235 Beach Road | Gisborne | Seaside 0302 | 2025-12-29 09:14 | 46020.3847 | 2025-12-29 10:21 | 46020.4313 | 0.12547 | 0.0018727 | 49 | 3283 | Unplanned | Unknown cause | Replace Fuses
917 |  | 1111-26 | Willow Flat | Wairoa | Raupunga 3101 | 2025-12-29 10:10 | 46020.4236 | 2025-12-30 17:35 | 46021.7326 | 0.37802 | 0.0062297 | 163 | 9891 | Unplanned | Vegetation | Tree over line but out of Zone. Branch broke off and broke centre phase
918 |  | 1112-26 | Waipiro Bay | Gisborne | Inland 0301 | 2025-12-29 14:37 | 46020.609 | 2025-12-30 15:22 | 46021.6403 | 0.28217 | 0.0026371 | 69 | 7383 | Unplanned | Adverse Environment | Slip caused tree to fall thru line. Note cross reference with SW 1115.
919 |  | 6276-26 | 673 Hokoroa Road | Gisborne | Tauwhareparae 0404 | 2025-12-29 15:26 | 46020.6431 | 2025-12-29 18:28 | 46020.7694 | 0.027823 | 0.00015288 | 4 | 728 | Unplanned | Unknown cause | Replace Fuses
920 |  | 1113-26 | W-O-Kuri | Gisborne | W O Kuri 1001 | 2025-12-29 17:00 | 46020.7083 | 2025-12-30 11:56 | 46021.4972 | 0.22771 | 0.0022167 | 58 | 5958 | Unplanned | Vegetation | Tree thru lines (heavy rain)
921 |  | 6277-26 | 2174 Tiniroto Road | Gisborne | W O Kuri 1001 | 2025-12-29 17:12 | 46020.7167 | 2025-12-30 18:36 | 46021.775 | 0.058246 | 3.8219e-05 | 1 | 1524 | Unplanned | Vegetation | Replace Fuses
922 |  | 1114-26 | Walkers Road | Gisborne | Ruatoria 0201 | 2025-12-29 18:42 | 46020.7792 | 2025-12-30 19:20 | 46021.8056 | 0.099369 | 0.00087904 | 23 | 2600 | Unplanned | Adverse Environment | Heavy rain caused slip in drain and pole J1720 fell over 45deg (Didn't trip)
923 |  | 6278-26 | 418 Te Hau Road | Gisborne | Whatatutu 1201 | 2025-12-30 08:38 | 46021.3597 | 2025-12-30 18:44 | 46021.7806 | 0.13896 | 0.00022931 | 6 | 3636 | Unplanned | Unknown cause | Replace Fuses
924 |  | 1115-26 | Kopuaroa Road | Gisborne | Inland 0301 | 2025-12-30 11:07 | 46021.4632 | 2025-12-30 16:41 | 46021.6951 | 0.90132 | 0.006115 | 160 | 23583 | Unplanned | Defective Equipment | Broken conductor (couldn't find cause). Note - cross reference with SW 1112
925 |  | 6279-26 | 976 Parikanapa Road | Gisborne | Parikanapa 1002 | 2025-12-31 15:09 | 46022.6312 | 2025-12-31 17:00 | 46022.7083 | 0.0042423 | 3.8219e-05 | 1 | 111 | Unplanned | Unknown cause | Replace Fuses
926 |  | 6280-26 | 33 Riripeti Street | Wairoa | Morere 3401 | 2026-01-01 17:36 | 46023.7333 | 2026-01-01 18:46 | 46023.7819 | 0.024078 | 0.00034397 | 9 | 630 | Unplanned | Unknown cause | Replace Fuses
927 |  | 6281-26 | 280 Ormond Valley Road | Gisborne | Waimata 0903 | 2026-01-02 22:29 | 46024.9368 | 2026-01-02 23:00 | 46024.9583 | 0.039098 | 0.0012612 | 33 | 1023 | Unplanned | Unknown cause | Replace Fuses
928 |  | 1118-26 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2026-01-03 07:26 | 46025.3097 | 2026-01-03 15:52 | 46025.6611 | 0.24712 | 0.00049685 | 13 | 6466 | Unplanned | Defective Equipment | H Pole J1906 failed
929 |  | 1119-26 | Raupunga | Wairoa | Raupunga 3101 | 2026-01-03 12:11 | 46025.5076 | 2026-01-03 22:00 | 46025.9167 | 3.3331 | 0.013071 | 342 | 87210 | Unplanned | Vegetation | Tree through HV conductor @ W1195 - W6346
930 |  | 1124-26 | 1354 Matawai Road | Gisborne | Waimata 0903 | 2026-01-03 15:00 | 46025.625 | 2026-01-04 14:56 | 46026.6222 | 0.10976 | 7.6438e-05 | 2 | 2872 | Unplanned | Lightning | Replace TX E293
931 |  | 1125-26 | Muriwai Township | Gisborne | Muriwai 0905 | 2026-01-03 15:03 | 46025.6271 | 2026-01-04 13:36 | 46026.5667 | 2.2066 | 0.0017963 | 47 | 57735 | Unplanned | Lightning | TX C153 , C154, C263 replaced after lightning strike
932 |  | 1123-26 | Taihamiti road | Gisborne | Whatatutu 1201 | 2026-01-03 15:59 | 46025.666 | 2026-01-04 10:59 | 46026.4576 | 0.17428 | 0.00015288 | 4 | 4560 | Unplanned | Lightning | Replaced TX F365 & TX F366
933 |  | 1127-26 | Te Kumi Stn | Gisborne | Hicks Bay 0102 | 2026-01-03 17:37 | 46025.734 | 2026-01-06 12:31 | 46028.5215 | 0.46023 | 0.00011466 | 3 | 12042 | Unplanned | Lightning | TX J398 hit by Lightning
934 |  | 1126-26 | Tawiri Road | Gisborne | Muriwai 0905 | 2026-01-03 17:55 | 46025.7465 | 2026-01-04 15:14 | 46026.6347 | 0.14665 | 0.00011466 | 3 | 3837 | Unplanned | Lightning | Replaced TX C414
935 |  | 1120-26 | Lavenham | Gisborne | Lavenham 0902 | 2026-01-03 19:06 | 46025.7958 | 2026-01-03 19:15 | 46025.8021 | 0.15891 | 0.017657 | 462 | 4158 | Unplanned | Vegetation | Removed tree branch from o/head conductor
936 |  | 1122-26 | Waipiro Bay | Gisborne | Inland 0301 | 2026-01-04 05:10 | 46026.2153 | 2026-01-07 16:09 | 46029.6729 | 0.30988 | 0.0026371 | 69 | 8108 | Unplanned | Vegetation | To Repair broken HV conductor between pole H2218-H2220, due to tree through the line
937 |  | 6282-26 | 173 Bailey Road | Gisborne | Waimata 0903 | 2026-01-04 15:49 | 46026.659 | 2026-01-04 17:20 | 46026.7222 | 0.0034779 | 3.8219e-05 | 1 | 91 | Unplanned | Unknown cause | Replace Fuses
938 |  | 1129-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2026-01-04 17:35 | 46026.7326 | 2026-01-05 15:09 | 46027.6312 | 0.57688 | 0.004357 | 114 | 15094 | Unplanned | Vegetation | To Repair broken HV line betwn Pole D3290 - D3291 due to tree through line.
939 |  | 6283-26 | 361 Stafford Road | Gisborne | Tahunga 1004 | 2026-01-05 11:59 | 46027.4993 | 2026-01-05 13:45 | 46027.5729 | 0.0040512 | 3.8219e-05 | 1 | 106 | Unplanned | Unknown cause | Replace Fuses
940 |  | 6284-26 | 28 Bellerby Road | Gisborne | W O Kuri 1001 | 2026-01-05 12:20 | 46027.5139 | 2026-01-05 12:57 | 46027.5396 | 0.0042423 | 0.00011466 | 3 | 111 | Unplanned | Unknown cause | Replace Fuses
941 |  | 6285-26 | 2072 Whangara Road | Gisborne | Dalton 0502 | 2026-01-05 14:44 | 46027.6139 | 2026-01-05 17:55 | 46027.7465 | 0.0146 | 7.6438e-05 | 2 | 382 | Unplanned | Unknown cause | Replace Fuses
942 |  | 1131-26 | Te Wera Road | Gisborne | Matawai 1204 | 2026-01-06 05:36 | 46028.2333 | 2026-01-06 12:03 | 46028.5021 | 0.90912 | 0.0027135 | 71 | 23787 | Unplanned | Wildlife | HV conductor down between poles F253 - F2139
943 |  | 1132-26 | Panikau Road | Gisborne | Dalton 0502 | 2026-01-06 13:15 | 46028.5521 | 2026-01-08 13:06 | 46030.5458 | 0.10973 | 3.8219e-05 | 1 | 2871 | Unplanned | Lightning | To replace faulty transformer A101 caused by lightning
944 |  | 1133-26 | Awapuni Rd / Aerodrome Road | Gisborne | Willows 0702 | 2026-01-06 17:58 | 46028.7486 | 2026-01-06 19:48 | 46028.825 | 0.16289 | 0.0038219 | 100 | 4262 | Unplanned | Unknown cause | No fault found
945 |  | 6286-26 | 180 College Road | Gisborne | Waimata 0903 | 2026-01-07 08:27 | 46029.3521 | 2026-01-07 09:15 | 46029.3854 | 0.0018345 | 3.8219e-05 | 1 | 48 | Unplanned | Unknown cause | Replace Fuses
946 |  | 6287-26 | 126 Bruce Road | Gisborne | Kanakanaia 1202 | 2026-01-07 08:42 | 46029.3625 | 2026-01-07 10:30 | 46029.4375 | 0.0082553 | 7.6438e-05 | 2 | 216 | Unplanned | Unknown cause | Replace Fuses
947 |  | 1119-26 | Raupunga | Wairoa | Raupunga 3101 | 2026-01-07 12:00 | 46029.5 | 2026-01-07 17:02 | 46029.7097 | 0.45912 | 0.0079496 | 208 | 12013 | Planned | Planned | Tree through HV conductor between W1195 - W6346
948 |  | 6288-26 | 71 Richardson Road | Gisborne | Tiniroto 1003 | 2026-01-07 18:04 | 46029.7528 | 2026-01-07 19:45 | 46029.8229 | 0.027021 | 0.00026753 | 7 | 707 | Unplanned | Lightning | Replace Fuses
949 |  | 6289-26 | 2740 Ihungia Road | Gisborne | Mata 0304 | 2026-01-07 18:59 | 46029.791 | 2026-01-08 02:00 | 46030.0833 | 0.28962 | 0.00068794 | 18 | 7578 | Unplanned | Lightning | Huge Lightning for an hour across whole area. Replaced fuses at TX H184, H185, H186, J190. Also HV fuses at isolations H188, H4494, H4118, H4195, H142, H272. All properties except Waitahaia W/shed TX H189 restored 8/1 2am put isolations H272 in. Had to go around to Mata to close. Cust rang 8/1 to say W/Shed still out. Checked all 3 fuses blown again. Notified Control. TX replaced 9th. 18 customers includes all beyond HV fuses H272 except 2 from TX H189, which went through control room
950 |  | 6290-26 | 20 Otoko School Road | Gisborne | Matawai 1204 | 2026-01-07 20:36 | 46029.8583 | 2026-01-08 10:10 | 46030.4236 | 0.062221 | 7.6438e-05 | 2 | 1628 | Unplanned | Lightning | Replace Fuses
951 |  | 6291-26 | 352 Mahaki Settlement Rd | Gisborne | Matawai 1204 | 2026-01-08 07:11 | 46030.2993 | 2026-01-08 08:22 | 46030.3486 | 0.0054271 | 7.6438e-05 | 2 | 142 | Unplanned | Unknown cause | Replace Fuses
952 |  | 1118-26 | Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2026-01-08 08:34 | 46030.3569 | 2026-01-08 15:14 | 46030.6347 | 0.47464 | 0.0018727 | 49 | 12419 | Planned | Planned | H-Pole J1906 Failed & Replaced
953 |  | 6292-26 | 79 Te Kowhai Road | Gisborne | Whatatutu 1201 | 2026-01-08 08:58 | 46030.3736 | 2026-01-08 10:58 | 46030.4569 | 0.018345 | 0.00015288 | 4 | 480 | Unplanned | Lightning | Replace Fuses
954 |  | 1134-26 | Waitahaia Road | Gisborne | Mata 0304 | 2026-01-08 10:08 | 46030.4222 | 2026-01-09 12:58 | 46031.5403 | 0.12307 | 7.6438e-05 | 2 | 3220 | Unplanned | Lightning | Lightnight strike TX H189
955 |  | 6293-26 | 172 Koranga Valley Road | Gisborne | Matawai 1204 | 2026-01-08 13:20 | 46030.5556 | 2026-01-08 15:05 | 46030.6285 | 0.012039 | 0.00011466 | 3 | 315 | Unplanned | Lightning | Replace Fuses
956 |  | 6294-26 | 1154 Matawai Road | Gisborne | Waimata 0903 | 2026-01-08 14:14 | 46030.5931 | 2026-01-08 16:26 | 46030.6847 | 0.085763 | 0.00064972 | 17 | 2244 | Unplanned | Unknown cause | Replace Fuses
957 |  | 1135-26 | East Cape road | Gisborne | Te Araroa 0103 | 2026-01-08 20:12 | 46030.8417 | 2026-01-08 21:08 | 46030.8806 | 0.007338 | 0.00084082 | 22 | 192 | Unplanned | Defective Equipment | Sectionaliser opened to facilitate closing HV fuses TX J221
958 |  | 1136-26 | Moanui road | Gisborne | Matawai 1204 | 2026-01-09 09:26 | 46031.3931 | 2026-01-12 14:30 | 46034.6042 | 0.88362 | 0.00019109 | 5 | 23120 | Unplanned | Defective Equipment | Wire down betweem poles F2503 & F2504
959 |  | 6295-26 | 200 Falkner Road | Gisborne | Tahora 1103 | 2026-01-09 09:59 | 46031.416 | 2026-01-09 10:49 | 46031.4507 | 0.0095547 | 0.00019109 | 5 | 250 | Unplanned | Unknown cause | Replace Fuses
960 |  | 6296-26 | 4574 Matawai Road | Gisborne | Matawai 1204 | 2026-01-10 07:53 | 46032.3285 | 2026-01-10 11:12 | 46032.4667 | 0.015211 | 7.6438e-05 | 2 | 398 | Unplanned | Unknown cause | Replace Fuses
961 |  | 6297-26 | 6 Hillcrest Street | Wairoa | Borough Two 3205 | 2026-01-11 08:45 | 46033.3646 | 2026-01-11 10:30 | 46033.4375 | 0.032104 | 0.00030575 | 8 | 840 | Unplanned | Wildlife | Replace Fuses
962 |  | 6298-26 | 27 Tahora Settlement Road | Gisborne | Tahora 1103 | 2026-01-11 14:51 | 46033.6188 | 2026-01-11 16:30 | 46033.6875 | 0.0037837 | 3.8219e-05 | 1 | 99 | Unplanned | Unknown cause | Replace Fuses
963 |  | 1138-26 | Waitahaia Road | Gisborne | Mata 0304 | 2026-01-12 02:11 | 46034.091 | 2026-01-13 13:25 | 46035.559 | 0.89784 | 0.0011084 | 29 | 23492 | Unplanned | Defective Equipment | To replace broken 11kV H-Pole structure H4498 (High Winds)
964 |  | 1140-26 | Tapuaeroa Road | Gisborne | Tiki Tiki 0206 | 2026-01-12 05:00 | 46034.2083 | 2026-01-12 15:46 | 46034.6569 | 0.83944 | 0.0012994 | 34 | 21964 | Unplanned | Vegetation | Tree through HV conductor Poles J2024 - J2025
965 |  | 1137-26 | Whatatutu Road | Gisborne | Whatatutu 1201 | 2026-01-12 05:32 | 46034.2306 | 2026-01-12 10:01 | 46034.4174 | 0.20902 | 0.0029046 | 76 | 5469 | Unplanned | Unknown cause | Recloser E863 tripped and locked out on E/F. No obvious fault was found upon carrying out sectionalised switching, and supply was restored.
966 |  | 1139-26 | Tutamoe road | Gisborne | Tauwhareparae 0404 | 2026-01-12 05:39 | 46034.2354 | 2026-01-12 18:15 | 46034.7604 | 0.65519 | 0.0019109 | 50 | 17143 | Unplanned | Vegetation | High winds blew pine tree through lines, snapped pole G2508
967 |  | 6299-26 | 90 Onepoto Road | Wairoa | Village 2002 | 2026-01-12 06:26 | 46034.2681 | 2026-01-12 09:24 | 46034.3917 | 0.37416 | 0.002102 | 55 | 9790 | Unplanned | Adverse Weather | Replace Fuses
968 |  | 6300-26 | 1262 Ohuka Road | Wairoa | Ruakituri 2003 | 2026-01-12 06:58 | 46034.2903 | 2026-01-12 10:22 | 46034.4319 | 0.19492 | 0.00095547 | 25 | 5100 | Unplanned | Adverse Weather | Replace Fuses
969 |  | 6301-26 | Mangataniwha Stn - End of Putere Rd | Wairoa | Raupunga 3101 | 2026-01-12 07:32 | 46034.3139 | 2026-01-12 10:50 | 46034.4514 | 0.075674 | 0.00038219 | 10 | 1980 | Unplanned | Adverse Weather | Patrol Line close HV fuse
970 |  | 1142-26 | Mangatu Road / Wairere Road | Gisborne | Whatatutu 1201 | 2026-01-12 08:10 | 46034.3403 | 2026-01-12 14:23 | 46034.5993 | 0.14256 | 0.00038219 | 10 | 3730 | Unplanned | Defective Equipment | To replace broken HV binder at pole E698 caused by high winds
971 |  | 6302-26 | 207 Rockhill Road | Gisborne | W O Kuri 1001 | 2026-01-12 08:29 | 46034.3535 | 2026-01-12 10:30 | 46034.4375 | 0.009249 | 7.6438e-05 | 2 | 242 | Unplanned | Unknown cause | Replace Fuses
972 |  | 6303-26 | 1048 Mangaoporo Road | Gisborne | Tiki Tiki 0206 | 2026-01-12 11:12 | 46034.4667 | 2026-01-12 16:40 | 46034.6944 | 0.012536 | 3.8219e-05 | 1 | 328 | Unplanned | Adverse Weather | HV fuse J2703 is betwn TX J224 & J220. Its not currently on schematic J
973 |  | 6304-26 | 6307 Matawai Road | Gisborne | Matawai 1204 | 2026-01-12 15:34 | 46034.6486 | 2026-01-12 18:14 | 46034.7597 | 0.01223 | 7.6438e-05 | 2 | 320 | Unplanned | Unknown cause | Replace Fuses
974 |  | 6305-26 | 2072 Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2026-01-12 17:32 | 46034.7306 | 2026-01-12 20:33 | 46034.8562 | 0.048423 | 0.00026753 | 7 | 1267 | Unplanned | Adverse Weather | Replace Fuses
975 |  | 6306-26 | Matahiia Road | Gisborne | Makarika 0204 | 2026-01-12 19:28 | 46034.8111 | 2026-01-12 20:20 | 46034.8472 | 0.017886 | 0.00034397 | 9 | 468 | Unplanned | Adverse Weather | Replace Fuses
976 |  | 6307-26 | 279 Falkner Road | Gisborne | Tahora 1103 | 2026-01-12 20:32 | 46034.8556 | 2026-01-13 07:50 | 46035.3264 | 0.051825 | 7.6438e-05 | 2 | 1356 | Unplanned | Vegetation | Advised customer trees need to be removed
977 |  | 3990-26 | Olivers Road | Gisborne | Matawai 1204 | 2026-01-13 09:08 | 46035.3806 | 2026-01-13 12:58 | 46035.5403 | 0.035161 | 0.00015288 | 4 | 460.0917 | Planned | Planned | Replace TX Pole F304
978 |  | 1146-26 | Tahora Road | Gisborne | Tahora 1103 | 2026-01-14 02:46 | 46036.1153 | 2026-01-14 05:21 | 46036.2229 | 0.32532 | 0.0021403 | 56 | 8512 | Unplanned | Unknown cause | Recloser D141 tripped and locked out. Supply restored after sectionalised switching and no faults found. To be patrolled again in daylight
979 |  | 6308-26 | 6307 Matawai Road | Gisborne | Matawai 1204 | 2026-01-14 09:03 | 46036.3771 | 2026-01-14 14:47 | 46036.616 | 0.026295 | 7.6438e-05 | 2 | 688 | Unplanned | Unknown cause | Replace Fuses
980 |  | 1147-26 | Wharekopae road | Gisborne | Tahora 1103 | 2026-01-14 20:30 | 46036.8542 | 2026-01-14 21:51 | 46036.9104 | 0.17336 | 0.0021403 | 56 | 4536 | Unplanned | Vegetation | Tree fire at pole D5048
981 |  | 3997-26 | Davis Rd / Oliver Rd | Gisborne | Matawai 1204 | 2026-01-15 09:04 | 46037.3778 | 2026-01-15 13:43 | 46037.5715 | 0.10663 | 0.00038219 | 10 | 1395.5733 | Planned | Planned | Replace HV Poles
982 |  | 1148-26 | Whakaangiangi Road | Gisborne | Awatere 0101 | 2026-01-15 10:10 | 46037.4236 | 2026-01-16 13:06 | 46038.5458 | 0.28351 | 0.0011848 | 31 | 7418 | Unplanned | Vegetation | Tree through HV line at J3048 - Wires down beyond
983 |  | 1149-26 | Taumata Road | Gisborne | Tahora 1103 | 2026-01-15 10:44 | 46037.4472 | 2026-01-15 20:22 | 46037.8486 | 0.43959 | 0.0055035 | 144 | 11502 | Unplanned | Wildlife | Sectionaliser D3416 tripped & locked out on E/F. After sectionalised switching, found a bird's remains on HV line at TX Pole D237. Replace dropout jumpers (burnt) and restored supply.
984 |  | 6309-26 | 1118 Wharerata Road | Gisborne | Muriwai 0905 | 2026-01-15 16:35 | 46037.691 | 2026-01-15 18:10 | 46037.7569 | 0.025416 | 0.00026753 | 7 | 665 | Unplanned | Unknown cause | Replace Fuses
985 |  | 6310-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-01-16 05:31 | 46038.2299 | 2026-01-16 07:09 | 46038.2979 | 0.026218 | 0.00026753 | 7 | 686 | Unplanned | Unknown cause | Replace Fuses
986 |  | 3999-26 | Puketiti Road | Gisborne | Inland 0301 | 2026-01-16 09:05 | 46038.3785 | 2026-01-16 11:28 | 46038.4778 | 0.054653 | 0.00038219 | 10 | 715.5733 | Planned | Planned | To replace 11kV poles H2178, H2182. Work was not completed due to lightning in the area.
987 |  | 1150-26 | Waimata Road | Gisborne | Waimata 0903 | 2026-01-16 09:46 | 46038.4069 | 2026-01-16 11:25 | 46038.4757 | 0.015135 | 0.00015288 | 4 | 396 | Unplanned | Unknown cause | To repair broken LV conductor betwn pole D4320-D4321. Possibly high load (truck) brushed through the LV line (Road crossing)
988 |  | 6311-26 | 1027 Wharekiri Road | Gisborne | Dalton 0502 | 2026-01-16 10:37 | 46038.4424 | 2026-01-16 12:32 | 46038.5222 | 0.0043952 | 3.8219e-05 | 1 | 115 | Unplanned | Lightning | Replace Fuses
989 |  | 6312-26 | 373 Tiniroto Road | Gisborne | Lavenham 0902 | 2026-01-16 11:45 | 46038.4896 | 2026-01-16 12:39 | 46038.5271 | 0.0061915 | 0.00011466 | 3 | 162 | Unplanned | Lightning | Replace Fuses
990 |  | 1151-26 | Lottin Point road | Gisborne | Hicks Bay 0102 | 2026-01-16 13:13 | 46038.5507 | 2026-01-21 11:22 | 46043.4736 | 0.56419 | 0.0015288 | 40 | 14762 | Unplanned | Vegetation | Tree through HV conductor J4203 - J4594 (ICP @ TX J466 on own generator)
991 |  | 6313-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-01-17 07:30 | 46039.3125 | 2026-01-17 09:18 | 46039.3875 | 0.028894 | 0.00026753 | 7 | 756 | Unplanned | Wildlife | Bird season has started Browns Beach Road
992 |  | 1153-26 | Wharerata Road, Manukuke | Gisborne | Muriwai 0905 | 2026-01-18 03:00 | 46040.125 | 2026-01-18 11:01 | 46040.459 | 0.28481 | 0.0061915 | 162 | 7452 | Unplanned | Third Party Interference | Car V's Pole C971. Held overnight, replaced during day - FENZ Call
993 |  | 1182-26 | 2332 Lake Road | Wairoa | Frasertown 3103 | 2026-01-18 15:30 | 46040.6458 | 2026-01-18 18:10 | 46040.7569 | 0.30269 | 0.0019109 | 50 | 7920 | Unplanned | Lightning | Lightning strike - Thurs 15/1. TX W1673 replaced
994 |  | 6314-26 | 8 Hillcrest, Wairoa | Wairoa | Borough Two 3205 | 2026-01-19 06:44 | 46041.2806 | 2026-01-19 07:15 | 46041.3021 | 0.0094783 | 0.00030575 | 8 | 248 | Unplanned | Unknown cause | Replaced 1 x HV fuse
995 |  | 6315-26 | 71 Richardson Road | Gisborne | Tiniroto 1003 | 2026-01-19 11:05 | 46041.4618 | 2026-01-19 13:10 | 46041.5486 | 0.0047774 | 3.8219e-05 | 1 | 125 | Unplanned | Unknown cause | Replace Fuses
996 |  | 1154-26 | McLean St | Wairoa | Brickworks 3201 | 2026-01-20 09:45 | 46042.4062 | 2026-01-20 09:58 | 46042.4153 | 0.006459 | 0.00049685 | 13 | 169 | Unplanned | Defective Equipment | To repair burnt LV Jumpers @ pole W1584
997 |  | 1155-26 | Mohaka Township road | Wairoa | Raupunga 3101 | 2026-01-20 10:57 | 46042.4563 | 2026-01-20 11:28 | 46042.4778 | 0.0047392 | 0.00015288 | 4 | 124 | Unplanned | Vegetation | Isolated HV line to cut and clear creepers from TX W1714 pole
998 |  | 6316-26 | 86 Cooper Road | Gisborne | Te Arai 0906 | 2026-01-20 11:50 | 46042.4931 | 2026-01-20 15:35 | 46042.6493 | 0.0085993 | 3.8219e-05 | 1 | 225 | Unplanned | Unknown cause | Replace Fuses
999 |  | 1156-26 | Tuakau Rd / Ihungia Rd | Gisborne | Mata 0304 | 2026-01-20 18:03 | 46042.7521 | 2026-01-21 13:59 | 46043.5826 | 0.11301 | 0.00087904 | 23 | 2957 | Unplanned | Vegetation | Tree through HV line betwn H1264-H141. Jumpers cut H1262 Power restored either side of fault
1000 |  | 6317-26 | 2198 Wharekopae Road | Gisborne | Ngatapa 1102 | 2026-01-21 06:27 | 46043.2688 | 2026-01-21 08:30 | 46043.3542 | 0.018804 | 0.00015288 | 4 | 492 | Unplanned | Unknown cause | Replace Fuses
1001 |  | 6318-26 | 2759 Bushy Knoll Rd | Gisborne | Tiniroto 1003 | 2026-01-21 06:42 | 46043.2792 | 2026-01-21 09:25 | 46043.3924 | 0.0062297 | 3.8219e-05 | 1 | 163 | Unplanned | Unknown cause | Replace Fuses
1002 |  | 3024-26 | Lake Road, Waihi | Wairoa | Frasertown 3103 | 2026-01-21 08:30 | 46043.3542 | 2026-01-21 09:18 | 46043.3875 | 0.19801 | 0.0042805 | 112 | 5181 | Planned | Planned | LFI installation @ W978 and W1794
1003 |  | 3024A-26 | Lake Road, Waihi | Wairoa | Frasertown 3103 | 2026-01-21 08:30 | 46043.3542 | 2026-01-21 10:59 | 46043.4576 | 0.14237 | 0.00095547 | 25 | 3725 | Planned | Planned | LFI installation @ W978 and W1794
1004 |  | 3025-26 | Otoi | Wairoa | Raupunga 3101 | 2026-01-21 12:00 | 46043.5 | 2026-01-21 12:22 | 46043.5153 | 0.018498 | 0.00084082 | 22 | 484 | Planned | Planned | Install LFI
1005 |  | 3026-26 | Lake Road | Wairoa | Frasertown 3103 | 2026-01-21 14:06 | 46043.5875 | 2026-01-21 14:36 | 46043.6083 | 0.0068794 | 0.00022931 | 6 | 180 | Planned | Planned | Install LFI @ W982
1006 |  | 1158-26 | Whatatutu Road | Gisborne | Whatatutu 1201 | 2026-01-21 15:16 | 46043.6361 | 2026-01-23 18:54 | 46045.7875 | 1.193 | 0.0060004 | 157 | 31216 | Unplanned | Vegetation | To repair broken HV conductor betwn Pole E783 - E771 due to tree through the line
1007 |  | 1159-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2026-01-21 19:20 | 46043.8056 | 2026-01-22 12:30 | 46044.5208 | 0.84491 | 0.0017963 | 47 | 22107 | Unplanned | Vegetation | Trees through HV line Poles D2687 - D2686
1008 |  | 1160-26 | Tauwhareparae / Tutamoe | Gisborne | Tauwhareparae 0404 | 2026-01-22 01:07 | 46044.0465 | 2026-01-23 14:01 | 46045.584 | 1.8021 | 0.0019109 | 50 | 47151 | Unplanned | Defective Equipment | Pole down byd ABS G222
1009 |  | 1161-26 | Hokoroa | Gisborne | Waimata 0903 | 2026-01-22 02:16 | 46044.0944 | 2026-01-22 17:48 | 46044.7417 | 0.1781 | 0.00019109 | 5 | 4660 | Unplanned | Defective Equipment | HV conductor down G583 - G584
1010 |  | 1162-26 | Paroa Road | Gisborne | Toko Tie 0401 | 2026-01-22 02:28 | 46044.1028 | 2026-01-22 12:49 | 46044.534 | 0.52215 | 0.0032104 | 84 | 13662 | Unplanned | Adverse Environment | Pole G1678 undercut by slip
1011 |  | 1163-26 | Ruakituri Road | Wairoa | Ruakituri 2003 | 2026-01-22 02:56 | 46044.1222 | 2026-01-23 20:14 | 46045.8431 | 1.6415 | 0.0034779 | 91 | 42949 | Unplanned | Vegetation | To replace damaged pole W7525 & Repair broken HV conductor due to tree through the line betwn W7525-W7527
1012 |  | 1164-26 | Lavenham Rd | Gisborne | Lavenham 0902 | 2026-01-22 07:36 | 46044.3167 | 2026-01-22 14:35 | 46044.6076 | 1.151 | 0.0062297 | 163 | 30116 | Unplanned | Vegetation | Tree in line D2107 - D2307
1013 |  | 1165-26 | Paparatu Road | Gisborne | Te Arai 0906 | 2026-01-22 07:47 | 46044.3243 | 2026-01-22 11:34 | 46044.4819 | 0.13014 | 0.00057328 | 15 | 3405 | Unplanned | Adverse Weather | Patrolled HV byd HV fuses C100 - All ok
1014 |  | 1170-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2026-01-22 10:10 | 46044.4236 | 2026-01-22 21:31 | 46044.8965 | 0.18219 | 0.00026753 | 7 | 4767 | Unplanned | Vegetation | To cut & clear pine tree through the line beyond HV fuses E1107
1015 |  | 1167-26 | East Cape road | Gisborne | Te Araroa 0103 | 2026-01-22 10:10 | 46044.4236 | 2026-01-26 14:26 | 46048.6014 | 5.295 | 0.00099369 | 26 | 138544 | Unplanned | Adverse Weather | Damaged to the power lines due to the adverse weather condition. Fallen pole J3700 & broken wire. Carried out Repair works and power was restored. Surrounding area affected by flooding & slips, delaying access.
1016 |  | 1171-26 | Tunanui Road | Wairoa | Mahia 3301 | 2026-01-22 10:52 | 46044.4528 | 2026-01-27 16:08 | 46049.6722 | 1.2037 | 0.00042041 | 11 | 31496 | Unplanned | Vegetation | To repair broken 11kV wire betwn Pole W9200-W9602 and W9620-W395 due to trees through the line
1017 |  | 6319-26 | 74 Scarlys Way | Gisborne | Dalton 0502 | 2026-01-22 13:41 | 46044.5701 | 2026-01-22 15:07 | 46044.6299 | 0.065737 | 0.00076438 | 20 | 1720 | Unplanned | Unknown cause | Replace Fuses
1018 |  | 6320-26 | 89 Scarlys Way | Gisborne | Dalton 0502 | 2026-01-22 16:06 | 46044.6708 | 2026-01-22 17:41 | 46044.7368 | 0.17065 | 0.0017963 | 47 | 4465 | Unplanned | Unknown cause | Replace Fuses
1019 |  | 6321-26 | 85 Cooper road | Gisborne | Lavenham 0902 | 2026-01-22 17:38 | 46044.7347 | 2026-01-22 19:50 | 46044.8264 | 0.090808 | 0.00068794 | 18 | 2376 | Unplanned | Unknown cause | Replace Fuses
1020 |  | 6322-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-01-22 19:37 | 46044.8174 | 2026-01-22 21:40 | 46044.9028 | 0.032907 | 0.00026753 | 7 | 861 | Unplanned | Unknown cause | Replace Fuses
1021 |  | 1172-26 | Wharf Rd / Matakaoa | Gisborne | Hicks Bay 0102 | 2026-01-22 19:58 | 46044.8319 | 2026-01-26 16:05 | 46048.6701 | 12.1528 | 0.012421 | 325 | 317978 | Unplanned | Adverse Weather | Pole down J3898 due to adverse weather (flood) and no access to the site
1022 |  | 1174-26 | Awamate Road / Aranui Road | Wairoa | Raupunga 3101 | 2026-01-23 06:41 | 46045.2785 | 2026-01-23 11:22 | 46045.4736 | 0.10503 | 0.00091726 | 24 | 2748 | Unplanned | Defective Equipment | Broken jumper W6122
1023 |  | 3022-26 | Waiotu Road | Gisborne | Mata 0304 | 2026-01-23 09:11 | 46045.3826 | 2026-01-23 12:03 | 46045.5021 | 0.013147 | 7.6438e-05 | 2 | 169.0129 | Planned | Planned | To upgrade TX H2552 to 30kVA
1024 |  | 3047-26 | Kitchener St / Clyde Street | Wairoa | Brickworks 3201 | 2026-01-23 09:25 | 46045.3924 | 2026-01-23 10:15 | 46045.4271 | 0.045863 | 0.00091726 | 24 | 1200 | Planned | Planned | To top up oil in Ring main unit W1072, W1073, W1074, W1075
1025 |  | 3022A-26 | Waiotu Road | Gisborne | Mata 0304 | 2026-01-23 10:06 | 46045.4208 | 2026-01-23 11:21 | 46045.4729 | 0.26084 | 0.0034779 | 91 | 2465.5453 | Planned | Planned | To upgrade TX H2552 to 30kVA
1026 |  | 3048-26 | Sturdee St / Apatu Street | Wairoa | Brickworks 3201 | 2026-01-23 10:33 | 46045.4396 | 2026-01-23 11:30 | 46045.4792 | 0.65179 | 0.011542 | 302 | 17054 | Planned | Planned | To top up oil in RMU W282, W283, W284
1027 |  | 1173-26 | Te Araroa Rd / Waione Road | Gisborne | Awatere 0101 | 2026-01-23 12:11 | 46045.5076 | 2026-01-23 14:05 | 46045.5868 | 0.23237 | 0.0034397 | 90 | 6080 | Unplanned | Defective Equipment | LV wires on ground. LV jumpers cut away
1028 |  | 3049-26 | Lochiel Street | Wairoa | Mahia 3301 | 2026-01-23 12:43 | 46045.5299 | 2026-01-23 13:26 | 46045.5597 | 0.10189 | 0.0023696 | 62 | 2666 | Planned | Planned | Top up oil ring main switches
1029 |  | 6323-26 | 207 Rockhill Road | Gisborne | W O Kuri 1001 | 2026-01-23 12:56 | 46045.5389 | 2026-01-23 15:50 | 46045.6597 | 0.01995 | 0.00011466 | 3 | 522 | Unplanned | Unknown cause | Replace Fuses
1030 |  | 6324-26 | 71 Richardson Road | Gisborne | Tiniroto 1003 | 2026-01-23 13:22 | 46045.5569 | 2026-01-23 19:58 | 46045.8319 | 0.10594 | 0.00026753 | 7 | 2772 | Unplanned | Unknown cause | Replace Fuses
1031 |  | 1175-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2026-01-23 18:55 | 46045.7882 | 2026-01-23 19:55 | 46045.8299 | 0.016052 | 0.00026753 | 7 | 420 | Unplanned | Defective Equipment | To replace burnt complete drop out holder D507
1032 |  | 1177-26 | Ruakituri Road / Whakapunaki | Wairoa | Ruakituri 2003 | 2026-01-24 02:56 | 46046.1222 | 2026-01-26 14:40 | 46048.6111 | 1.5796 | 0.0025225 | 66 | 41330 | Unplanned | Vegetation | Tree through the HV line at pole W7513 - W7512
1033 |  | 1176-26 | SH2 Road, Wairoa | Wairoa | Morere 3401 | 2026-01-24 08:10 | 46046.3403 | 2026-01-24 08:44 | 46046.3639 | 0.11045 | 0.0032486 | 85 | 2890 | Unplanned | Vegetation | To repair broken LV conductor betwn Poles W435-W8315. Isolated HV for safety reasons. Ref SW 5347
1034 |  | 6325-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-01-24 11:17 | 46046.4701 | 2026-01-24 12:50 | 46046.5347 | 0.024881 | 0.00026753 | 7 | 651 | Unplanned | Unknown cause | Replace Fuses
1035 |  | 6326-26 | 585 & 582 Kiore Road | Gisborne | Tauwhareparae 0404 | 2026-01-24 19:44 | 46046.8222 | 2026-01-25 08:40 | 46047.3611 | 0.23726 | 0.00030575 | 8 | 6208 | Unplanned | Adverse Weather | Checked all sets of isolation fuses G142 & G1523 on way in. Nothing hanging/no tails. Test at TX G144 lost HV, same at TX G143. Pulled fuses H1523 ok. Pulled fuses H142, found 1 blown. Hadn't dropped out. Replaced & Checked. All customers OK now.
1036 |  | 3050-26 | Marine Parade / Carroll St / Bridge St | Wairoa | Borough Two 3205 | 2026-01-25 09:17 | 46047.3868 | 2026-01-25 11:08 | 46047.4639 | 0.40302 | 0.0036308 | 95 | 10545 | Planned | Planned | To top up oil in RMU at A-Park
1037 |  | 3050-26 | Ormond Rd / Carroll St / Crarer St | Wairoa | Borough Two 3205 | 2026-01-25 09:19 | 46047.3882 | 2026-01-25 11:08 | 46047.4639 | 0.3291 | 0.0030193 | 79 | 8611 | Unplanned | Defective Equipment | Faulty ABS W930 fail to open
1038 |  | 3051-26 | Marine Parade | Wairoa | Borough Two 3205 | 2026-01-25 11:54 | 46047.4958 | 2026-01-25 12:19 | 46047.5132 | 0.00095547 | 3.8219e-05 | 1 | 25 | Planned | Planned | Top up oil in Ring Main Unit (W232, W233, W234)
1039 |  | 3052-26 | Kitchener Street / Queen Street | Wairoa | Borough Two 3205 | 2026-01-25 12:31 | 46047.5215 | 2026-01-25 13:29 | 46047.5618 | 0.64506 | 0.011122 | 291 | 16878 | Planned | Planned | To Top-up oil in Ring main unit
1040 |  | 1179-26 | Waiapu Road | Gisborne | Makarika 0204 | 2026-01-25 12:41 | 46047.5285 | 2026-01-25 13:20 | 46047.5556 | 0.0014905 | 3.8219e-05 | 1 | 39 | Unplanned | Vegetation | To cut & clear trees from the HV/LV line betwn Pole H1845-H3030
1041 |  | 1180-26 | Mangapoike Road | Wairoa | Frasertown 3103 | 2026-01-26 05:57 | 46048.2479 | 2026-01-26 09:21 | 46048.3896 | 0.56136 | 0.0027518 | 72 | 14688 | Unplanned | Wildlife | To repair broken HV conductor betwn pole W6565-W6566 due to bird strike
1042 |  | 6327-26 | 112 Haliburton Road | Wairoa | Raupunga 3101 | 2026-01-26 09:21 | 46048.3896 | 2026-01-26 12:35 | 46048.5243 | 0.0074145 | 3.8219e-05 | 1 | 194 | Unplanned | Unknown cause | Replace Fuses
1043 |  | 6328-26 | 15 Takapau Road | Gisborne | Tauwhareparae 0404 | 2026-01-26 10:35 | 46048.441 | 2026-01-26 12:42 | 46048.5292 | 0.03883 | 0.00030575 | 8 | 1016 | Unplanned | Unknown cause | 11kV line needs maintenance uneven sag etc and poles replaced
1044 |  | 6329-26 | 1200 Wharerata Road | Gisborne | Muriwai 0905 | 2026-01-27 08:59 | 46049.3743 | 2026-01-27 10:45 | 46049.4479 | 0.028358 | 0.00026753 | 7 | 742 | Unplanned | Wildlife | Replace Fuses
1045 |  | 6330-26 | 187 Berry Road | Gisborne | Tiniroto 1003 | 2026-01-27 13:07 | 46049.5465 | 2026-01-27 14:20 | 46049.5972 | 0.03906 | 0.00053507 | 14 | 1022 | Unplanned | Unknown cause | Replace Fuses
1046 |  | 3011-26 | Mata Road | Gisborne | Mata 0304 | 2026-01-28 09:00 | 46050.375 | 2026-01-28 14:58 | 46050.6236 | 0.36931 | 0.0010319 | 27 | 4835.5019 | Planned | Planned | To replace 11kV poles H1215 & H1214
1047 |  | 3019-26 | Mahanga Road | Wairoa | Mahia 3301 | 2026-01-28 10:05 | 46050.4201 | 2026-01-28 11:53 | 46050.4951 | 0.35498 | 0.0032868 | 86 | 2372.7734 | Planned | Planned | To connect HV cable at pole W9875 and liven new RMU
1048 |  | 1183-26 | Whangara / Fox Street | Gisborne | Whangara 0506 | 2026-01-28 11:23 | 46050.4743 | 2026-01-28 12:06 | 46050.5042 | 0.61311 | 0.022587 | 591 | 16042 | Unplanned | Unknown cause | Whangara feeder CB A472 tripped. No obvious fault was located upon sectionlised switching
1049 |  | 6331-26 | 1 Piripaua Road | Wairoa | Frasertown 3103 | 2026-01-28 21:04 | 46050.8778 | 2026-01-28 22:49 | 46050.9507 | 0.056182 | 0.00053507 | 14 | 1470 | Unplanned | Unknown cause | Replace Fuses
1050 |  | 6332-26 | 28 Bellerby Road | Gisborne | W O Kuri 1001 | 2026-01-29 05:06 | 46051.2125 | 2026-01-29 08:45 | 46051.3646 | 0.05859 | 0.00026753 | 7 | 1533 | Unplanned | Unknown cause | Replace Fuses
1051 |  | 6333-26 | 75A Sponge Bay Road | Gisborne | Wainui 0504 | 2026-01-29 05:57 | 46051.2479 | 2026-01-29 07:41 | 46051.3201 | 0.023849 | 0.00022931 | 6 | 624 | Unplanned | Unknown cause | Replace Fuses
1052 |  | 3012-26 | Mata Road | Gisborne | Mata 0304 | 2026-01-29 09:00 | 46051.375 | 2026-01-29 14:31 | 46051.6049 | 0.3411 | 0.0010319 | 27 | 4466.2001 | Planned | Planned | To replace 11kV poles
1053 |  | 1184-26 | Tiniroto Road | Gisborne | W O Kuri 1001 | 2026-01-29 09:49 | 46051.409 | 2026-01-29 11:15 | 46051.4688 | 0.06245 | 0.0016816 | 44 | 1634 | Unplanned | Human Error | Faultman closed HV fuses D4390 @ round 0949hrs and around same time CB D674 tripped on first OD. HV fuses blown on TX D177
1054 |  | 3015-26 | Whakarau Road | Gisborne | Matawai 1204 | 2026-01-30 09:02 | 46052.3764 | 2026-01-30 11:54 | 46052.4958 | 0.07231 | 0.00042041 | 11 | 946.763 | Planned | Planned | To replace 11kV poles
1055 |  | 3072-26 | Pehiri Road | Gisborne | Tahunga 1004 | 2026-01-30 09:38 | 46052.4014 | 2026-01-30 13:22 | 46052.5569 | 0.11985 | 0.00053507 | 14 | 3136 | Planned | Planned | 11kV deenergised and isolated for safety. Team working on 50kV Pole D905
1056 |  | 6334-26 | Huiarua Stn, Tokomaru Bay | Gisborne | Mata 0304 | 2026-01-31 09:54 | 46053.4125 | 2026-01-31 13:00 | 46053.5417 | 0.0071087 | 3.8219e-05 | 1 | 186 | Unplanned | Unknown cause | Replace Fuses
1057 |  | 6335-26 | 1175 Waiapu Road, Mangatuna | Gisborne | Toko Tie 0401 | 2026-02-01 10:02 | 46054.4181 | 2026-02-01 11:09 | 46054.4646 | 0.007682 | 0.00011466 | 3 | 201 | Unplanned | Wildlife | Replace Fuses
1058 |  | 1186-26 | JNL Sub | Gisborne | JNL LS 1620 | 2026-02-01 19:02 | 46054.7931 | 2026-02-01 20:15 | 46054.8438 | 0.00279 | 3.8219e-05 | 1 | 73 | Unplanned | Defective Equipment | VT Insulator failure on 50kV Network @ JNL CB C84
1059 |  | 1187-26 | Disraeli Street | Gisborne | Gladstone 0607 | 2026-02-02 06:06 | 46055.2542 | 2026-02-03 19:24 | 46056.8083 | 0.39366 | 0.0019109 | 50 | 10300 | Unplanned | Defective Equipment | HV cable crutch blow-out
1060 |  | 3040-26 | Lytton Road | Gisborne | Chalmers 0707 | 2026-02-02 08:34 | 46055.3569 | 2026-02-02 09:45 | 46055.4062 | 0.0027135 | 3.8219e-05 | 1 | 35.5017 | Planned | Planned | Shut to drop line to remove trees
1061 |  | 1188-26 | Kopuapounamu | Gisborne | Awatere 0101 | 2026-02-03 08:12 | 46056.3417 | 2026-02-03 13:33 | 46056.5646 | 0.25102 | 0.0018345 | 48 | 6568 | Unplanned | Defective Equipment | Broken insulator tracking caused conductor to fail
1062 |  | 3032-26 | Waitangi Road | Gisborne | Kanakanaia 1202 | 2026-02-03 09:00 | 46056.375 | 2026-02-03 14:08 | 46056.5889 | 0.30606 | 0.00099369 | 26 | 4007.9788 | Planned | Planned | Replace Remote SW E1066 & Recloser E1066. Replace HV pole E959
1063 |  | 3039-26 | Bloomfield Road | Gisborne | Bell 1406 | 2026-02-03 09:01 | 46056.3757 | 2026-02-03 10:09 | 46056.4229 | 0.13774 | 0.0020256 | 53 | 1805.6501 | Planned | Planned | Clearing trees betwn poles C5247 - C5243
1064 |  | 3014-26 | Mata Road | Gisborne | Mata 0304 | 2026-02-03 09:02 | 46056.3764 | 2026-02-03 16:17 | 46056.6785 | 0.44877 | 0.0010319 | 27 | 5875.8627 | Planned | Planned | Replace HV Poles
1065 |  | 6636-26 | 2000 Ruakituri Road | Wairoa | Ruakituri 2003 | 2026-02-03 15:12 | 46056.6333 | 2026-02-03 18:10 | 46056.7569 | 0.013606 | 7.6438e-05 | 2 | 356 | Unplanned | Vegetation | Tree came down and clipped wires
1066 |  | 3042-26 | Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2026-02-04 10:04 | 46057.4194 | 2026-02-04 13:21 | 46057.5563 | 0.12341 | 0.00064972 | 17 | 1615.038 | Planned | Planned | Install new TX J565
1067 |  | 3076-26 | East Cape road | Gisborne | Te Araroa 0103 | 2026-02-04 12:00 | 46057.5 | 2026-02-04 14:10 | 46057.5903 | 0.11366 | 0.00087904 | 23 | 2974 | Planned | Planned | Isolate for pole relocation to allow craning-in Bailey bridge
1068 |  | 1190-26 | Wairoa / North Clyde | Wairoa | Borough Two 3205 | 2026-02-04 18:23 | 46057.766 | 2026-02-04 20:50 | 46057.8681 | 2.509 | 0.025225 | 660 | 65649 | Unplanned | Unknown cause | Patrolled all HV OH on feeder. 1 x X-arm @ pole W3223 failure but not cause of fault (requires replacement). No cause identified.
1069 |  | 6637-26 | 539 SH2 RD3 | Wairoa | Raupunga 3101 | 2026-02-05 06:47 | 46058.2826 | 2026-02-05 08:15 | 46058.3438 | 0.016816 | 0.00019109 | 5 | 440 | Unplanned | Unknown cause | Replace Fuses
1070 |  | 3082-26 | Matanui Road | Gisborne | Tauwhareparae 0404 | 2026-02-05 09:02 | 46058.3764 | 2026-02-05 14:19 | 46058.5965 | 0.048462 | 0.00015288 | 4 | 1268 | Planned | Planned | Replace poles
1071 |  | 1191-26 | 117 Waingake Road | Gisborne | Te Arai 0906 | 2026-02-05 12:19 | 46058.5132 | 2026-02-05 13:09 | 46058.5479 | 0.019109 | 0.00038219 | 10 | 500 | Unplanned | Defective Equipment | Broken LV wire, isolated at TX
1072 |  | 3040B-26 | Lytton Road | Gisborne | Chalmers 0707 | 2026-02-05 14:01 | 46058.584 | 2026-02-05 15:37 | 46058.6507 | 0.003669 | 3.8219e-05 | 1 | 96 | Unplanned | Human Error | Shut to drop line to remove trees. Planned work carried out on date not advertised.
1073 |  | 6638-26 | 335 Pakowhai Road | Gisborne | Tauwhareparae 0404 | 2026-02-05 14:15 | 46058.5938 | 2026-02-05 17:45 | 46058.7396 | 0.064208 | 0.00030575 | 8 | 1680 | Unplanned | Wildlife | Patrolled line old poles and uneven sag through out.
1074 |  | 1192-26 | Ngamotu Road | Wairoa | Affco 3202 | 2026-02-06 21:06 | 46059.8792 | 2026-02-07 00:21 | 46060.0146 | 0.24384 | 0.0013377 | 35 | 6380 | Unplanned | Defective Equipment | Unknown fault caused conductor to fail
1075 |  | 6639-26 | 16 Ngamotu Road | Wairoa | Affco 3202 | 2026-02-06 21:06 | 46059.8792 | 2026-02-07 00:05 | 46060.0035 | 0.20524 | 0.0011466 | 30 | 5370 | Unplanned | Unknown cause | Possible faulty conductor
1076 |  | 1193-26 | Tolaga Bay Sub | Gisborne | Rototahi 0403 | 2026-02-07 00:07 | 46060.0049 | 2026-02-07 00:17 | 46060.0118 | 0.082553 | 0.0082553 | 216 | 2160 | Unplanned | Defective Equipment | Blown jumper at 50kV ABS A3
1077 |  | 1193-26 | Tolaga Bay Sub | Gisborne | Town 0402 | 2026-02-07 00:07 | 46060.0049 | 2026-02-07 00:20 | 46060.0139 | 0.10235 | 0.0078731 | 206 | 2678 | Unplanned | Defective Equipment | Blown jumper at 50kV ABS A3
1078 |  | 1193-26 | Tolaga Bay Sub | Gisborne | Toko Tie 0401 | 2026-02-07 00:07 | 46060.0049 | 2026-02-07 00:22 | 46060.0153 | 0.048156 | 0.0032104 | 84 | 1260 | Unplanned | Defective Equipment | Blown jumper at 50kV ABS A3
1079 |  | 1193-26 | Tolaga Bay Sub | Gisborne | Tauwhareparae 0404 | 2026-02-07 00:07 | 46060.0049 | 2026-02-07 00:23 | 46060.016 | 0.085611 | 0.0053507 | 140 | 2240 | Unplanned | Defective Equipment | Blown jumper at 50kV ABS A3
1080 |  | 1193-26 | Tolaga Bay Sub | Gisborne | Tolaga Bay LS 0420 | 2026-02-07 00:07 | 46060.0049 | 2026-02-07 00:17 | 46060.0118 | 0.00038219 | 3.8219e-05 | 1 | 10 | Unplanned | Defective Equipment | Blown jumper at 50kV ABS A3
1081 |  | 6640-26 | 71a Onepoto Road | Wairoa | Village 2002 | 2026-02-07 06:15 | 46060.2604 | 2026-02-07 09:20 | 46060.3889 | 0.38888 | 0.002102 | 55 | 10175 | Unplanned | Unknown cause | Replace Fuses
1082 |  | 6641-26 | 17 Arero Road | Gisborne | Mata 0304 | 2026-02-07 07:48 | 46060.325 | 2026-02-07 08:35 | 46060.3576 | 0.0035926 | 7.6438e-05 | 2 | 94 | Unplanned | Unknown cause | Replace Fuses
1083 |  | 6642-26 | 1173 Waimata Valley Road | Gisborne | Waimata 0903 | 2026-02-08 10:02 | 46061.4181 | 2026-02-08 11:30 | 46061.4792 | 0.0033633 | 3.8219e-05 | 1 | 88 | Unplanned | Unknown cause | Replace Fuses
1084 |  | 6643-26 | 25 Tuparoa Road | Gisborne | Ruatoria 0201 | 2026-02-09 08:01 | 46062.334 | 2026-02-09 10:54 | 46062.4542 | 0.14546 | 0.00084082 | 22 | 3806 | Unplanned | Unknown cause | Replace Fuses
1085 |  | 3033-26 | Pilmer road | Gisborne | Bushmere 0805 | 2026-02-09 08:37 | 46062.359 | 2026-02-09 12:01 | 46062.5007 | 0.04678 | 0.00022931 | 6 | 612.1445 | Planned | Planned | Replace LV pole C4955
1086 |  | 6644-26 | 1710 Ruakituri Road | Wairoa | Ruakituri 2003 | 2026-02-09 17:55 | 46062.7465 | 2026-02-09 19:20 | 46062.8056 | 0.012994 | 0.00015288 | 4 | 340 | Unplanned | Lightning | Replace Fuses
1087 |  | 1194-26 | Waimata Valley | Gisborne | Waimata 0903 | 2026-02-09 21:19 | 46062.8882 | 2026-02-12 14:41 | 46065.6118 | 0.97787 | 0.0054271 | 142 | 25586 | Unplanned | Vegetation | Pine tree branch on line betwn E1002-E1019. Difficult terrain, jumpers cut and generator installed until tree could be cleared
1088 |  | 1195-26 | Brickworks feeder | Wairoa | Brickworks 3201 | 2026-02-10 03:24 | 46063.1417 | 2026-02-10 05:15 | 46063.2188 | 1.4847 | 0.025989 | 680 | 38846 | Unplanned | Unknown cause | Brickworks feeder tripped. No obvious fault was located after sectionalised switching
1089 |  | 3061-26 | Matawai Road, McMillan Road | Gisborne | Te Karaka 1203 | 2026-02-10 08:33 | 46063.3562 | 2026-02-10 14:14 | 46063.5931 | 0.62557 | 0.0018345 | 48 | 8199.0136 | Planned | Planned | Replace Stub poles
1090 |  | 3034-26 | King Road | Gisborne | Waimata 0903 | 2026-02-10 08:36 | 46063.3583 | 2026-02-10 11:38 | 46063.4847 | 0.076514 | 0.00042041 | 11 | 1001.4856 | Planned | Planned | Replace LV pole C4966
1091 |  | 3083-26 | Fernside - Matanui Road | Gisborne | Tauwhareparae 0404 | 2026-02-10 09:02 | 46063.3764 | 2026-02-10 13:33 | 46063.5646 | 0.041429 | 0.00015288 | 4 | 1084 | Planned | Planned | Replace HV poles
1092 |  | 3010-26 | Putere Road | Wairoa | Raupunga 3101 | 2026-02-10 09:05 | 46063.3785 | 2026-02-10 12:40 | 46063.5278 | 0.0082171 | 3.8219e-05 | 1 | 107.5057 | Planned | Planned | Replace defected pole W5145
1093 |  | 6645-26 | 1833 Ruakituri Valley Road | Wairoa | Ruakituri 2003 | 2026-02-10 22:44 | 46063.9472 | 2026-02-11 07:30 | 46064.3125 | 0.040206 | 7.6438e-05 | 2 | 1052 | Unplanned | Lightning | Replace Fuses
1094 |  | 3035-26 | Royd Rd East | Gisborne | Haisman 0804 | 2026-02-11 08:13 | 46064.3424 | 2026-02-11 11:48 | 46064.4917 | 0.049303 | 0.00022931 | 6 | 645.1479 | Planned | Planned | Replace LV pole C1589
1095 |  | 6646-26 | 53 Mangaroa Road | Wairoa | Ruakituri 2003 | 2026-02-11 08:29 | 46064.3535 | 2026-02-11 10:21 | 46064.4313 | 0.017122 | 0.00015288 | 4 | 448 | Unplanned | Lightning | Replace Fuses
1096 |  | 3016-26 | Fernside road | Gisborne | Tauwhareparae 0404 | 2026-02-11 09:01 | 46064.3757 | 2026-02-11 13:35 | 46064.566 | 0.041888 | 0.00015288 | 4 | 548.1009 | Planned | Planned | Replace HV Poles
1097 |  | 6647-26 | 408 East Cape road | Gisborne | Te Araroa 0103 | 2026-02-11 12:17 | 46064.5118 | 2026-02-11 13:34 | 46064.5653 | 0.070629 | 0.00091726 | 24 | 1848 | Unplanned | Human Error | Replace Fuses
1098 |  | 3036-26 | Glenelg road | Gisborne | Waimata 0903 | 2026-02-11 13:19 | 46064.5549 | 2026-02-11 15:57 | 46064.6646 | 0.21739 | 0.0013759 | 36 | 2847.913 | Planned | Planned | Replace HV pole D2813
1099 |  | 6648-26 | 603 Waitangi Road | Gisborne | Kanakanaia 1202 | 2026-02-11 19:10 | 46064.7986 | 2026-02-11 22:21 | 46064.9313 | 0.087598 | 0.00045863 | 12 | 2292 | Unplanned | Unknown cause | Replace Fuses
1100 |  | 1196-26 | Wharekopae road | Gisborne | Tahora 1103 | 2026-02-12 07:56 | 46065.3306 | 2026-02-12 18:47 | 46065.7826 | 2.0078 | 0.0078731 | 206 | 52534 | Unplanned | Defective Equipment | Trees betwn D2974-D135 removed. Faulty recloser @ D141. Removed and Jumpered through
1101 |  | 3017-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2026-02-12 08:34 | 46065.3569 | 2026-02-12 14:54 | 46065.6208 | 0.15976 | 0.00042041 | 11 | 2090.8787 | Planned | Planned | Replace HV poles
1102 |  | 3037-26 | Cameron Road | Gisborne | Nelson 0803 | 2026-02-12 08:39 | 46065.3604 | 2026-02-12 11:51 | 46065.4938 | 0.088057 | 0.00045863 | 12 | 1152.5779 | Planned | Planned | Replace LV pole C1463
1103 |  | 3088-26 | Putere Stoney Creek Forest | Wairoa | Raupunga 3101 | 2026-02-12 09:01 | 46065.3757 | 2026-02-12 13:29 | 46065.5618 | 0.010243 | 3.8219e-05 | 1 | 268 | Planned | Planned | Replace 11kV poles
1104 |  | 1198-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2026-02-13 06:52 | 46066.2861 | 2026-02-13 11:25 | 46066.4757 | 0.43027 | 0.0034779 | 91 | 11258 | Unplanned | Defective Equipment | Blown HV Lightning arrestor @ TX J371
1105 |  | 3067-26 | Tiniroto Road | Gisborne | Tiniroto 1003 | 2026-02-13 09:02 | 46066.3764 | 2026-02-13 13:09 | 46066.5479 | 0.02832 | 0.00011466 | 3 | 741 | Planned | Planned | Replace existing pole D3844
1106 |  | 3089-26 | Putere Stoney Creek Forest | Wairoa | Raupunga 3101 | 2026-02-13 09:07 | 46066.3799 | 2026-02-13 11:18 | 46066.4708 | 0.0050067 | 3.8219e-05 | 1 | 131 | Planned | Planned | Replace HV poles
1107 |  | 1199-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2026-02-13 21:52 | 46066.9111 | 2026-02-14 15:45 | 46067.6562 | 1.4741 | 0.0048538 | 127 | 38570 | Unplanned | Defective Equipment | Cracked insulator pole J2827
1108 |  | 1200-26 | Whakarau | Gisborne | Matawai 1204 | 2026-02-14 05:51 | 46067.2438 | 2026-02-16 15:44 | 46069.6556 | 0.20638 | 0.0025607 | 67 | 10520 | Unplanned | Defective Equipment | Broken pole F2097 required replacement. Jumpers cut and power restored until new pole can be installed.
1109 |  | 1202-26 | Te Araroa Township | Gisborne | Te Araroa 0103 | 2026-02-14 10:49 | 46067.4507 | 2026-02-15 15:50 | 46068.6597 | 0.40818 | 0.0011466 | 30 | 10680 | Unplanned | Defective Equipment | Faulty pole mount TX. Installed generator.
1110 |  | 1201-26 | Koranga Valley Road | Gisborne | Matawai 1204 | 2026-02-14 11:07 | 46067.4632 | 2026-02-14 16:02 | 46067.6681 | 0.059316 | 0.00099369 | 26 | 1552 | Unplanned | Defective Equipment | Isolation required to replace glass fuxes at TX F267
1111 |  | 1203-26 | Waimata Valley Road | Gisborne | Waimata 0903 | 2026-02-14 19:05 | 46067.7951 | 2026-02-15 00:13 | 46068.009 | 0.45225 | 0.021938 | 574 | 11833 | Unplanned | Third Party Interference | Car V Pole - Conductor down at D1409 & pole D1410 replaced
1112 |  | 1204-26 | Otoko, Makaretu Road | Gisborne | Matawai 1204 | 2026-02-14 22:49 | 46067.9507 | 2026-02-15 13:19 | 46068.5549 | 1.4048 | 0.0021403 | 56 | 36757 | Unplanned | Vegetation | High wind blew tree through line
1113 |  | 1205-26 | East Cape Road | Gisborne | Te Araroa 0103 | 2026-02-15 05:39 | 46068.2354 | 2026-02-15 13:54 | 46068.5792 | 0.43333 | 0.00099369 | 26 | 11338 | Unplanned | Defective Equipment | Cross arm broken on pole J3746 and conductor down beyond J497 due to storm.
1114 |  | 1206-26 | Tawera Rd / Paparatu Road | Gisborne | Te Arai 0906 | 2026-02-15 16:02 | 46068.6681 | 2026-02-18 16:50 | 46071.7014 | 1.8154 | 0.0030575 | 80 | 47501 | Unplanned | Vegetation | Trees through HV conductor C789-C790
1115 |  | 1207-26 | Top end of Mata Road | Gisborne | Mata 0304 | 2026-02-15 17:58 | 46068.7486 | 2026-02-16 13:51 | 46069.5771 | 1.2959 | 0.0011848 | 31 | 33907 | Unplanned | Vegetation | Out of zone plantation tree damaged conductor H1097-H1096
1116 |  | 1208-26 | Mata Road | Gisborne | Mata 0304 | 2026-02-15 18:09 | 46068.7562 | 2026-02-15 20:17 | 46068.8451 | 0.081292 | 0.001223 | 32 | 2127 | Unplanned | Adverse Weather | HV conductor wrap (due to high wind) @ Pole H777. Cleared using insulated stick
1117 |  | 1209-26 | Onenui, Mahia | Wairoa | Mahia 3301 | 2026-02-15 19:41 | 46068.8201 | 2026-02-20 19:30 | 46073.8125 | 1.1191 | 0.0025607 | 67 | 29282 | Unplanned | Defective Equipment | To repair broken HV conductor between pole W9405-W1109 and betwn W1114-W9425
1118 |  | 1210-26 | Papatu Road, Waingake Rd, Taurau Valley | Gisborne | Te Arai 0906 | 2026-02-15 21:23 | 46068.891 | 2026-02-15 23:10 | 46068.9653 | 0.7914 | 0.0081406 | 213 | 20707 | Unplanned | Unknown cause | Sectionalised feeder and restored to normal
1119 |  | 1211-26 | Whakarau | Gisborne | Matawai 1204 | 2026-02-16 03:22 | 46069.1403 | 2026-02-16 15:44 | 46069.6556 | 0.58165 | 0.0018345 | 48 | 15219 | Unplanned | Vegetation | Trees through conductor F2066-F2068. Note jumpers were cut at F2096 in SW1200 on 14/2/26
1120 |  | 1212-26 | Mata Road | Gisborne | Mata 0304 | 2026-02-16 05:46 | 46069.2403 | 2026-02-16 08:27 | 46069.3521 | 0.091726 | 0.001223 | 32 | 2400 | Unplanned | Vegetation | Pine tree through line (no customers betwn H123-H345)
1121 |  | 1215-26 | Ruatoria Township | Gisborne | Ruatoria 0201 | 2026-02-16 06:36 | 46069.275 | 2026-02-16 10:45 | 46069.4479 | 0.44728 | 0.0017963 | 47 | 11703 | Unplanned | Defective Equipment | LV cable fault ran thru & blew HV fuses. Installed Generator
1122 |  | 6649-26 | 1542 Panikau Road | Gisborne | Dalton 0502 | 2026-02-16 06:37 | 46069.2757 | 2026-02-16 10:44 | 46069.4472 | 0.075521 | 0.00030575 | 8 | 1976 | Unplanned | Adverse Weather | Replace Fuses
1123 |  | 1213-26 | Willow Flat Rd, Wairoa | Wairoa | Raupunga 3101 | 2026-02-16 06:52 | 46069.2861 | 2026-02-19 16:56 | 46072.7056 | 0.21708 | 0.010166 | 266 | 5680 | Unplanned | Vegetation | To cut trees and repair broken HV conductor betwn Pole W5231-W5233
1124 |  | 3053-26 | Williams Road | Gisborne | Muriwai 0905 | 2026-02-16 08:42 | 46069.3625 | 2026-02-16 10:57 | 46069.4563 | 0.041277 | 0.00030575 | 8 | 540.1651 | Planned | Planned | To replace pole C2478
1125 |  | 1214-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2026-02-16 10:44 | 46069.4472 | 2026-02-16 11:45 | 46069.4896 | 0.0023314 | 3.8219e-05 | 1 | 61 | Unplanned | Defective Equipment | To repair hanging wires after storm
1126 |  | 1216-26 | Whakaki | Wairoa | Nuhaka 3203 | 2026-02-16 11:33 | 46069.4812 | 2026-02-16 12:11 | 46069.5076 | 0.059545 | 0.001567 | 41 | 1558 | Unplanned | Adverse Environment | Drain gave way after heavy rain. Pole fell over 45deg, isolated to stand up, temp stay fitted.
1127 |  | 6650-26 | 761 Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2026-02-17 08:47 | 46070.366 | 2026-02-17 13:12 | 46070.55 | 0.020256 | 7.6438e-05 | 2 | 530 | Unplanned | Defective Equipment | Neighbour had a cable fault took out HV fuse
1128 |  | 3060-26 | Armstrong Road | Gisborne | Whatatutu 1201 | 2026-02-17 09:03 | 46070.3771 | 2026-02-17 13:54 | 46070.5792 | 0.23356 | 0.0008026 | 21 | 3057.9523 | Planned | Planned | To install sectionaliser E867
1129 |  | 6651-26 | 3260 SH 2, Nuhaka | Wairoa | Morere 3401 | 2026-02-17 10:52 | 46070.4528 | 2026-02-17 16:00 | 46070.6667 | 0.047086 | 0.00015288 | 4 | 1232 | Unplanned | Vegetation | Address of the house looks like it is fed from W111 but ICPs belong to W314
1130 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Haisman 0804 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 23:21 | 46070.9729 | 2.5632 | 0.037531 | 982 | 67066 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1131 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Kanakanaia 1202 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:57 | 46070.8313 | 0.29417 | 0.0068412 | 179 | 7697 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1132 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Te Karaka 1203 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:57 | 46070.8313 | 0.30732 | 0.007147 | 187 | 8041 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1133 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Matawai 1204 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:57 | 46070.8313 | 0.6245 | 0.014523 | 380 | 16340 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1134 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Whatatutu 1201 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:57 | 46070.8313 | 0.40264 | 0.0093637 | 245 | 10535 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1135 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Puha LS 1220 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:57 | 46070.8313 | 0.0016434 | 3.8219e-05 | 1 | 43 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1136 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Te Arai 0906 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.37883 | 0.0090197 | 236 | 9912 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1137 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Lavenham 0902 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.7416 | 0.017657 | 462 | 19404 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1138 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Muriwai 0905 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.67579 | 0.01609 | 421 | 17682 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1139 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Waimata 0903 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 1.0498 | 0.024995 | 654 | 27468 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1140 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Patutahi LS 0920 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.0016052 | 3.8219e-05 | 1 | 42 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1141 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | W O Kuri 1001 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.070629 | 0.0016816 | 44 | 1848 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1142 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Parikanapa 1002 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.049761 | 0.0011848 | 31 | 1302 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1143 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Tiniroto 1003 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.19262 | 0.0045863 | 120 | 5040 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1144 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Tahunga 1004 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.075444 | 0.0017963 | 47 | 1974 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1145 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Pehiri LS 1020 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.0016052 | 3.8219e-05 | 1 | 42 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1146 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Totangi 1101 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.020868 | 0.00049685 | 13 | 546 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1147 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Tahora 1103 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.23275 | 0.0055418 | 145 | 6090 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1148 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Ngatapa 1102 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.10594 | 0.0025225 | 66 | 2772 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1149 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Ngatapa LS 1120 | 2026-02-17 19:14 | 46070.8014 | 2026-02-17 19:56 | 46070.8306 | 0.0016052 | 3.8219e-05 | 1 | 42 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1150 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Nelson 0803 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:52 | 46070.8278 | 0.80959 | 0.0352 | 921 | 21183 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1151 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Campion 0802 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:52 | 46070.8278 | 0.64961 | 0.028244 | 739 | 16997 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1152 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Bushmere 0805 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:52 | 46070.8278 | 0.16086 | 0.0069941 | 183 | 4209 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1153 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Makaraka LS 0820 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:52 | 46070.8278 | 0.00087904 | 3.8219e-05 | 1 | 23 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1154 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Dunstan 1403 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:56 | 46070.8306 | 0.012383 | 0.00045863 | 12 | 324 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1155 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | JNL_A 1405 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:56 | 46070.8306 | 0.019606 | 0.00072616 | 19 | 513 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1156 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Bell 1406 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:56 | 46070.8306 | 0.24044 | 0.008905 | 233 | 6291 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1157 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Waipaoa 1408 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:56 | 46070.8306 | 0.0051596 | 0.00019109 | 5 | 135 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1158 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Solander 0706 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.038525 | 0.0016052 | 42 | 1008 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1159 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Cedenco A 0704 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.0027518 | 0.00011466 | 3 | 72 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1160 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Innes 0705 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.028435 | 0.0011848 | 31 | 744 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1161 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Chalmers 0707 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.66042 | 0.027518 | 720 | 17280 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1162 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Lytton 0701 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.064208 | 0.0026753 | 70 | 1680 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1163 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Willows 0702 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.077049 | 0.0032104 | 84 | 2016 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1164 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | Elgin 0703 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.86222 | 0.035926 | 940 | 22560 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1165 |  | 1219-26 | Gis-Maka / Bk Ormond Rd | Gisborne | JNL LS 1620 | 2026-02-17 19:29 | 46070.8118 | 2026-02-17 19:53 | 46070.8285 | 0.00091726 | 3.8219e-05 | 1 | 24 | Unplanned | Third Party Interference | Car v's 50/11kV pole C5728. Extra customer numbers and longer duration due to a switching error.
1166 |  | 1220-26 | King Road | Gisborne | Bushmere 0805 | 2026-02-18 07:36 | 46071.3167 | 2026-02-18 09:02 | 46071.3764 | 0.016434 | 0.00019109 | 5 | 430 | Unplanned | Third Party Interference | To Repair broken LV conductor betwn Pole C5550-C5551 caused by a truck
1167 |  | 3068-26 | Te Araroa Road | Gisborne | Tiki Tiki 0206 | 2026-02-18 09:03 | 46071.3771 | 2026-02-18 11:02 | 46071.4597 | 0.027288 | 0.00022931 | 6 | 351.0805 | Planned | Planned | To upgrade TX J38
1168 |  | 6652-26 | 16 Mangaoae Road | Gisborne | Kanakanaia 1202 | 2026-02-18 10:44 | 46071.4472 | 2026-02-18 11:45 | 46071.4896 | 0.018651 | 0.00030575 | 8 | 488 | Unplanned | Unknown cause | Replace Fuses
1169 |  | 3069-26 | Te Araroa Road | Gisborne | Awatere 0101 | 2026-02-18 13:03 | 46071.5437 | 2026-02-18 14:41 | 46071.6118 | 0.12735 | 0.0012994 | 34 | 1668.1649 | Planned | Planned | Install new TX J907
1170 |  | 6653-26 | Cnr James St & Ayton St | Gisborne | Haisman 0804 | 2026-02-19 05:45 | 46072.2396 | 2026-02-19 06:40 | 46072.2778 | 0.16396 | 0.0029811 | 78 | 4290 | Unplanned | Unknown cause | Replace Fuses
1171 |  | 3020-26 | Bushy Knoll Road | Gisborne | Tiniroto 1003 | 2026-02-19 08:49 | 46072.3674 | 2026-02-19 14:23 | 46072.5993 | 0.063826 | 0.00019109 | 5 | 835.1596 | Planned | Planned | Replace HV Poles
1172 |  | 3054-26 | Gordon Road | Gisborne | Te Arai 0906 | 2026-02-19 09:04 | 46072.3778 | 2026-02-19 14:36 | 46072.6083 | 0.15226 | 0.00045863 | 12 | 1992.9136 | Planned | Planned | To replace 11kV poles C2738 & C2741
1173 |  | 1222-26 | Arakihi Road | Gisborne | Tauwhareparae 0404 | 2026-02-19 18:24 | 46072.7667 | 2026-02-19 21:40 | 46072.9028 | 0.31168 | 0.0079878 | 209 | 8155 | Unplanned | Defective Equipment | To repair broken HV line betwn Pole G1586-G1587
1174 |  | 6654-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-02-19 20:55 | 46072.8715 | 2026-02-19 21:30 | 46072.8958 | 0.0093637 | 0.00026753 | 7 | 245 | Unplanned | Unknown cause | Replace Fuses
1175 |  | 3100-26 | Whakaki Road | Wairoa | Nuhaka 3203 | 2026-02-20 08:48 | 46073.3667 | 2026-02-20 12:12 | 46073.5083 | 0.31966 | 0.001567 | 41 | 8364 | Planned | Planned | To relocate 11kV pole W8807
1176 |  | 3065-26 | Kanakanaia Road | Gisborne | Kanakanaia 1202 | 2026-02-20 09:03 | 46073.3771 | 2026-02-20 13:46 | 46073.5736 | 0.80478 | 0.0028664 | 75 | 21057 | Planned | Planned | To install new recloser F1072
1177 |  | 3044-26 | Tutamoe Road | Gisborne | Tauwhareparae 0404 | 2026-02-20 09:04 | 46073.3778 | 2026-02-20 13:26 | 46073.5597 | 0.10013 | 0.00038219 | 10 | 1310.5733 | Planned | Planned | To replace 11kV poles G2500 & G2503
1178 |  | 3055-26 | Toreohaua Road | Gisborne | Lavenham 0902 | 2026-02-20 09:06 | 46073.3792 | 2026-02-20 13:12 | 46073.55 | 0.018804 | 7.6438e-05 | 2 | 246.0252 | Planned | Planned | To replace pole D5344, D5345
1179 |  | 3081-26 | Tuaraki road | Gisborne | Muriwai 0905 | 2026-02-20 09:07 | 46073.3799 | 2026-02-20 12:15 | 46073.5104 | 0.16526 | 0.00087904 | 23 | 1991.2488 | Planned | Planned | To Upgrade Transformer C122
1180 |  | 1223-26 | Waingake Road | Gisborne | Te Arai 0906 | 2026-02-20 14:00 | 46073.5833 | 2026-02-20 15:32 | 46073.6472 | 0.27789 | 0.0090197 | 236 | 7271 | Unplanned | Defective Equipment | To repair blown HV jumper at pole C3631
1181 |  | 3056-26 | Taurau Valley Road | Gisborne | Te Arai 0906 | 2026-02-21 09:15 | 46074.3854 | 2026-02-21 10:41 | 46074.4451 | 0.18078 | 0.002102 | 55 | 2369.9713 | Planned | Planned | To Replace HV Pole C2609
1182 |  | 3057-26 | Rakaukaka Road | Gisborne | Te Arai 0906 | 2026-02-21 12:33 | 46074.5229 | 2026-02-21 14:18 | 46074.5958 | 0.028091 | 0.00026753 | 7 | 367.6124 | Planned | Planned | To Replace HV pole C2855
1183 |  | 3079-26 | Lyndhurst Street | Gisborne | Anzac 0604 | 2026-02-22 08:14 | 46075.3431 | 2026-02-22 15:13 | 46075.634 | 1.7775 | 0.0042423 | 111 | 23353.3882 | Planned | Planned | To install new RMU
1184 |  | 6655-26 | 208 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-02-22 21:01 | 46075.8757 | 2026-02-22 21:45 | 46075.9062 | 0.011771 | 0.00026753 | 7 | 308 | Unplanned | Unknown cause | Replace Fuses
1185 |  | 6656-26 | 280 Ormond Valley Road | Gisborne | Waimata 0903 | 2026-02-23 07:15 | 46076.3021 | 2026-02-23 09:15 | 46076.3854 | 0.15135 | 0.0012612 | 33 | 3960 | Unplanned | Unknown cause | Replace Fuses
1186 |  | 3098-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2026-02-23 08:31 | 46076.3549 | 2026-02-23 13:19 | 46076.5549 | 0.77317 | 0.0029811 | 78 | 10136.5876 | Planned | Planned | To replace recloser D141
1187 |  | 1231-26 | Wharekopae Road | Gisborne | Tahora 1103 | 2026-02-23 08:31 | 46076.3549 | 2026-02-23 13:01 | 46076.5424 | 0.051596 | 0.00019109 | 5 | 1350 | Unplanned | Human Error | TX D147 missed off advert for planned switching # 3098
1188 |  | 3066-26 | Lloyd George Road | Gisborne | Tamarau 0503 | 2026-02-23 09:04 | 46076.3778 | 2026-02-23 11:58 | 46076.4986 | 0.0133 | 7.6438e-05 | 2 | 174.0133 | Planned | Planned | Upgrade TX A496
1189 |  | 3045-26 | Stafford Street | Gisborne | Harris 1502 | 2026-02-23 10:01 | 46076.4174 | 2026-02-23 15:37 | 46076.6507 | 1.3484 | 0.004013 | 105 | 17710.7892 | Planned | Planned | To replace 11kV pole B1365
1190 |  | 6657-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-02-23 20:39 | 46076.8604 | 2026-02-23 21:45 | 46076.9062 | 0.017657 | 0.00026753 | 7 | 462 | Unplanned | Unknown cause | Replace Fuses
1191 |  | 3084-26 | Wainui Road | Gisborne | Port A 1501 | 2026-02-24 07:03 | 46077.2937 | 2026-02-24 07:47 | 46077.3243 | 0.01009 | 0.00022931 | 6 | 132.0303 | Planned | Planned | Replensh oil in RMU A411 - A412 - A413 - A480
1192 |  | 3071-26 | Puketiti Road | Gisborne | Inland 0301 | 2026-02-24 09:03 | 46077.3771 | 2026-02-24 14:13 | 46077.5924 | 0.11848 | 0.00038219 | 10 | 1550.5924 | Planned | Planned | Replace 11kV poles
1193 |  | 3041-26 | Koranga Valley Road, Moanui Road | Gisborne | Matawai 1204 | 2026-02-24 09:07 | 46077.3799 | 2026-02-24 13:08 | 46077.5472 | 0.23948 | 0.00099369 | 26 | 3137.2629 | Planned | Planned | Replace HV poles
1194 |  | 1224-26 | Kakariki Farm Road | Wairoa | Raupunga 3101 | 2026-02-24 12:21 | 46077.5146 | 2026-02-24 13:17 | 46077.5535 | 0.0021403 | 3.8219e-05 | 1 | 56 | Unplanned | Third Party Interference | O/head LV conductor contacted by Skidder driver at site
1195 |  | 3087-26 | Kowhai St / Abbott St | Gisborne | Gladstone 0607 | 2026-02-24 12:35 | 46077.5243 | 2026-02-24 13:05 | 46077.5451 | 0.092872 | 0.0030957 | 81 | 1218.7613 | Planned | Planned | Replenish oil @ RMU B1895, B1896, B1897
1196 |  | 6658-26 | 256 Wairere Road | Gisborne | Whatatutu 1201 | 2026-02-24 21:14 | 46077.8847 | 2026-02-25 00:53 | 46078.0368 | 0.0837 | 0.00038219 | 10 | 2190 | Unplanned | Unknown cause | Livened 256 Wairere Road @ 13:24
1197 |  | 3091-26 | Kowhai St / Abbott St | Gisborne | Gladstone 0607 | 2026-02-25 14:35 | 46078.6076 | 2026-02-25 15:05 | 46078.6285 | 0.28435 | 0.0094783 | 248 | 7440 | Planned | Planned | To top up oil in RMU B1057, B1058, F782, B783, B784
1198 |  | 6659-26 | 213 Browns Beach Road | Gisborne | Muriwai 0905 | 2026-02-25 20:26 | 46078.8514 | 2026-02-25 21:43 | 46078.9049 | 0.0206 | 0.00026753 | 7 | 539 | Unplanned | Unknown cause | Replace Fuses
1199 |  | 3092-26 | Lytton Road, Bulwer road | Gisborne | Elgin 0703 | 2026-02-26 07:03 | 46079.2937 | 2026-02-26 07:38 | 46079.3181 | 0.4441 | 0.012689 | 332 | 11620 | Planned | Planned | SW/GR maintenance oil top up
1200 |  | 3074-26 | Puketiti Road | Gisborne | Inland 0301 | 2026-02-26 09:04 | 46079.3778 | 2026-02-26 14:08 | 46079.5889 | 0.11619 | 0.00038219 | 10 | 1520.5809 | Planned | Planned | Replace HV poles
1201 |  | 1226-26 | Te Araroa Road | Gisborne | Hicks Bay 0102 | 2026-02-26 12:12 | 46079.5083 | 2026-02-26 13:05 | 46079.5451 | 0.38448 | 0.0086375 | 226 | 10060 | Unplanned | Adverse Environment | Tree in slip in contact of O/Head HV conductor
1202 |  | 1227-26 | Marine Parade | Wairoa | Borough Two 3205 | 2026-02-26 12:32 | 46079.5222 | 2026-02-26 15:51 | 46079.6604 | 0.0076056 | 3.8219e-05 | 1 | 199 | Unplanned | Defective Equipment | RMS W858 failed during operation. Ring Main unit replaced
1203 |  | 6660-26 | 23 Mahia Avenue | Wairoa | Borough One 3204 | 2026-02-26 14:34 | 46079.6069 | 2026-02-26 17:07 | 46079.7132 | 0.15204 | 0.00099369 | 26 | 3978 | Unplanned | Unknown cause | Replace Fuses
1204 |  | 6661-26 | 81 King Road | Gisborne | Bushmere 0805 | 2026-02-26 18:08 | 46079.7556 | 2026-02-26 19:37 | 46079.8174 | 0.017007 | 0.00019109 | 5 | 445 | Unplanned | Unknown cause | Replace Fuses
1205 |  | 3086-26 | Waiapu Rd | Gisborne | Toko Tie 0401 | 2026-02-27 09:06 | 46080.3792 | 2026-02-27 13:38 | 46080.5681 | 0.2391 | 0.00087904 | 23 | 3130.7496 | Planned | Planned | To replace ABS G82
1206 |  | 6662-26 | 89 Matakaoa Road | Gisborne | Hicks Bay 0102 | 2026-02-28 06:55 | 46081.2882 | 2026-02-28 10:34 | 46081.4403 | 0.15903 | 0.00072616 | 19 | 4161 | Unplanned | Unknown cause | Replace Fuses
1207 |  | 1229-26 | Pa Road | Gisborne | Dalton 0502 | 2026-02-28 09:04 | 46081.3778 | 2026-02-28 11:15 | 46081.4688 | 0.15521 | 0.0011848 | 31 | 4061 | Unplanned | Adverse Environment | River washed out Pole footing - Pole relocated
1208 |  | 3106-26 | College Road | Gisborne | Ruatoria - Te Araroa 50kV J12 | 2026-02-28 09:33 | 46081.3979 | 2026-02-28 13:23 | 46081.5576 | 0.087904 | 0.00038219 | 10 | 2300 | Planned | Planned | Replace pole J1275
1209 |  | 1230-26 | Tolaga Bay | Gisborne | Rototahi 0403 | 2026-02-28 22:37 | 46081.9424 | 2026-02-28 22:55 | 46081.9549 | 0.1486 | 0.0082553 | 216 | 3888 | Unplanned | Unknown cause | A & B OC fault - Loss of Comms A8
1210 |  | 1230-26 | Tolaga Bay | Gisborne | Town 0402 | 2026-02-28 22:37 | 46081.9424 | 2026-02-28 22:55 | 46081.9549 | 0.14172 | 0.0078731 | 206 | 3708 | Unplanned | Unknown cause | A & B OC fault - Loss of Comms A8
1211 |  | 1230-26 | Tolaga Bay | Gisborne | Toko Tie 0401 | 2026-02-28 22:37 | 46081.9424 | 2026-02-28 22:56 | 46081.9556 | 0.060998 | 0.0032104 | 84 | 1596 | Unplanned | Unknown cause | A & B OC fault - Loss of Comms A8
1212 |  | 1230-26 | Tolaga Bay | Gisborne | Tauwhareparae 0404 | 2026-02-28 22:37 | 46081.9424 | 2026-02-28 22:57 | 46081.9563 | 0.10701 | 0.0053507 | 140 | 2800 | Unplanned | Unknown cause | A & B OC fault - Loss of Comms A8
1213 |  | 1230-26 | Tolaga Bay | Gisborne | Tolaga Bay LS 0420 | 2026-02-28 22:37 | 46081.9424 | 2026-02-28 22:54 | 46081.9542 | 0.00064972 | 3.8219e-05 | 1 | 17 | Unplanned | Unknown cause | A & B OC fault - Loss of Comms A8
1214 |  | 3101-26 | Parkinson Street | Gisborne | Solander 0706 | 2026-03-01 08:02 | 46082.3347 | 2026-03-01 09:17 | 46082.3868 | 0.068794 | 0.00091726 | 24 | 1800 | Planned | Planned | Top up oil RMU
1215 |  | 6663-26 | 49 Pitcher Road | Gisborne | Te Karaka 1203 | 2026-03-01 12:45 | 46082.5312 | 2026-03-01 15:30 | 46082.6458 | 0.044143 | 0.00026753 | 7 | 1155 | Unplanned | Wildlife | Replace Fuses
1216 |  | 1232-26 | Morere Road | Wairoa | Morere 3401 | 2026-03-03 00:30 | 46084.0208 | 2026-03-03 12:41 | 46084.5285 | 0.37925 | 0.0061533 | 161 | 9923 | Unplanned | Vegetation | Tree through line @ W137-W8383
1217 |  | 6664-26 | 63 Thomas Road | Gisborne | Rototahi 0403 | 2026-03-03 09:56 | 46084.4139 | 2026-03-03 11:13 | 46084.4674 | 0.0088286 | 0.00011466 | 3 | 231 | Unplanned | Vegetation | Replace Fuses
1218 |  | 6665-26 | 18 Puia Street | Gisborne | Inland 0301 | 2026-03-03 10:54 | 46084.4542 | 2026-03-03 16:21 | 46084.6813 | 0.024995 | 7.6438e-05 | 2 | 654 | Unplanned | Vegetation | Kept blowing HV isolation fuses. Cabbage trees & vines wrapped around LV lines. Cut away main section. Still 25m odd requires cutting
1219 |  | 1233-26 | Puia St / Waipiro Rd | Gisborne | Inland 0301 | 2026-03-03 11:50 | 46084.4931 | 2026-03-03 16:23 | 46084.6826 | 0.020868 | 7.6438e-05 | 2 | 546 | Unplanned | Vegetation | To cut & clear trees from HV/LV lines between Pole H323-H2853
1220 |  | 6666-26 | 418 Waiatai Road | Wairoa | Nuhaka 3203 | 2026-03-03 20:53 | 46084.8701 | 2026-03-03 21:52 | 46084.9111 | 0.029314 | 0.00049685 | 13 | 767 | Unplanned | Unknown cause | Replace Fuses
1221 |  | 3099-26 | Herschell Street | Gisborne | Kaiti Sub 05 | 2026-03-04 09:00 | 46085.375 | 2026-03-04 15:12 | 46085.6333 | 2.5023 | 0.0067265 | 176 | 31893.0969 | Planned | Planned | Kaiti Sub Bus outage
1222 |  | 3058-26 | Kaiaua Road | Gisborne | Toko Tie 0401 | 2026-03-04 09:05 | 46085.3785 | 2026-03-04 11:59 | 46085.4993 | 0.1064 | 0.0006115 | 16 | 2784 | Planned | Planned | To replace 11kV Poles G766, G767, G768
1223 |  | 3102-26 | Mangahauini Gorge Waiapu Road | Gisborne | Inland 0301 | 2026-03-04 09:08 | 46085.3806 | 2026-03-04 15:56 | 46085.6639 | 0.32746 | 0.0008026 | 21 | 8568 | Planned | Planned | To relocate 11kV poles H2262 & H2264
1224 |  | 6667-26 | 764 Kakariki Farm Road | Wairoa | Raupunga 3101 | 2026-03-04 13:53 | 46085.5785 | 2026-03-04 16:44 | 46085.6972 | 0.0065354 | 3.8219e-05 | 1 | 171 | Unplanned | Wildlife | Replace Fuses
1225 |  | 6668-26 | 755 Oliver Road | Gisborne | Matawai 1204 | 2026-03-04 14:53 | 46085.6201 | 2026-03-04 18:30 | 46085.7708 | 0.066348 | 0.00030575 | 8 | 1736 | Unplanned | Unknown cause | Replace Fuses
1226 |  | 3096-26 | Waimata Valley Road | Gisborne | Waimata 0903 | 2026-03-05 08:37 | 46086.359 | 2026-03-05 15:38 | 46086.6514 | 0.35914 | 0.00087904 | 23 | 4700.5931 | Planned | Planned | Install new Sectionaliser E289
1227 |  | 3059-26 | Kaiaua Road | Gisborne | Toko Tie 0401 | 2026-03-05 09:02 | 46086.3764 | 2026-03-05 13:13 | 46086.5507 | 0.15349 | 0.0006115 | 16 | 2009.4676 | Planned | Planned | To replace 11kV poles
1228 |  | 1235-26 | Te Wera / Tahora Rd | Gisborne | Matawai 1204 | 2026-03-05 20:48 | 46086.8667 | 2026-03-06 15:56 | 46087.6639 | 0.69807 | 0.0040894 | 107 | 18265 | Unplanned | Defective Equipment | Bulls knocked over red tag hardwood pole
1229 |  | 3094-26 | Tiniroto Road | Wairoa | Frasertown 3103 | 2026-03-06 08:33 | 46087.3562 | 2026-03-06 13:50 | 46087.5764 | 0.33923 | 0.0010701 | 28 | 4443.3935 | Planned | Planned | Replace HV poles
1230 |  | 3130-26 | Kirkpatrick Road - Bolitho Road | Gisborne | Waimata 0903 | 2026-03-06 09:00 | 46087.375 | 2026-03-06 13:08 | 46087.5472 | 0.31278 | 0.0012612 | 33 | 8184 | Planned | Planned | Check & Test HV cable & clean grease
1231 |  | 1237-26 | Waihi | Wairoa | Frasertown 3103 | 2026-03-09 13:35 | 46090.566 | 2026-03-09 19:01 | 46090.7924 | 0.49838 | 0.0015288 | 40 | 13040 | Unplanned | Third Party Interference | Landowner drove digger thru lines with bucket up
1232 |  | 6669-26 | 413 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2026-03-09 19:32 | 46090.8139 | 2026-03-09 20:58 | 46090.8736 | 0.029582 | 0.00034397 | 9 | 774 | Unplanned | Unknown cause | Replace Fuses
1233 |  | 3077-26 | Mata Road | Gisborne | Mata 0304 | 2026-03-10 09:01 | 46091.3757 | 2026-03-10 14:00 | 46091.5833 | 0.30785 | 0.0010319 | 27 | 4031.1891 | Planned | Planned | To replace 11kV poles H175
1234 |  | 3108-26 | Shelley Road | Gisborne | Whangara 0506 | 2026-03-10 09:04 | 46091.3778 | 2026-03-10 15:42 | 46091.6542 | 0.53239 | 0.0013377 | 35 | 6974.3168 | Planned | Planned | Replace & Upgrade TX B724
1235 |  | 3095-26 | Iwitea - Waitai Road | Wairoa | Nuhaka 3203 | 2026-03-10 09:07 | 46091.3799 | 2026-03-10 16:58 | 46091.7069 | 1.2132 | 0.0025989 | 68 | 12007.4577 | Planned | Planned | Replace Remote ABS with Recloser
1236 |  | 6670-26 | 518 Waitangi Road | Gisborne | Kanakanaia 1202 | 2026-03-10 11:28 | 46091.4778 | 2026-03-10 13:27 | 46091.5604 | 0.0045481 | 3.8219e-05 | 1 | 119 | Unplanned | Unknown cause | Replace Fuses
1237 |  | 6671-26 | 599 Arakihi Road | Gisborne | Tauwhareparae 0404 | 2026-03-10 12:45 | 46091.5312 | 2026-03-10 16:35 | 46091.691 | 0.079113 | 0.00034397 | 9 | 2070 | Unplanned | Unknown cause | Replace Fuses
1238 |  | 6672-26 | 16 Mangaoae Road | Gisborne | Kanakanaia 1202 | 2026-03-11 06:31 | 46092.2715 | 2026-03-11 09:14 | 46092.3847 | 0.049838 | 0.00030575 | 8 | 1304 | Unplanned | Unknown cause | Replace Fuses
1239 |  | 1238-26 | Darwin Rd, Whatakapoa | Gisborne | Whangara 0506 | 2026-03-11 11:21 | 46092.4729 | 2026-03-11 13:10 | 46092.5486 | 1.339 | 0.022587 | 591 | 35036 | Unplanned | Unknown cause | Line patrol unable to identify cause of fault
1240 |  | 6673-26 | 218 Pakowhai Road | Gisborne | Muriwai 0905 | 2026-03-11 14:20 | 46092.5972 | 2026-03-11 16:27 | 46092.6854 | 0.077661 | 0.0006115 | 16 | 2032 | Unplanned | Unknown cause | Replace Fuses
1241 |  | 3109-26 | Mahanga Road | Wairoa | Mahia 3301 | 2026-03-13 09:04 | 46094.3778 | 2026-03-13 15:44 | 46094.6556 | 1.33 | 0.0033251 | 87 | 17457.8559 | Planned | Planned | Install new Transformer W1477
1242 |  | 1239-26 | Bushmere Rd / Bloomfield Rd | Gisborne | Bushmere 0805 | 2026-03-13 18:47 | 46094.7826 | 2026-03-14 00:36 | 46095.025 | 0.68049 | 0.0069941 | 183 | 17805 | Unplanned | Third Party Interference | To replace broken 11kV pole C5050 - Car vs pole
1243 |  | 6674-26 | 99 Lake Road | Gisborne | Lavenham 0902 | 2026-03-14 07:52 | 46095.3278 | 2026-03-14 10:10 | 46095.4236 | 0.094936 | 0.00068794 | 18 | 2484 | Unplanned | Unknown cause | Replace Fuses
1244 |  | 3116-26 | Carroll St | Wairoa | Borough Two 3205 | 2026-03-14 09:03 | 46095.3771 | 2026-03-14 12:00 | 46095.5 | 0.52765 | 0.0029811 | 78 | 6923.5784 | Planned | Planned | To remove faulty ABS W930 and Install new ABS at pole W3137
1245 |  | 6675-26 | 975 Parikanapa Road | Gisborne | Parikanapa 1002 | 2026-03-14 11:34 | 46095.4819 | 2026-03-14 13:28 | 46095.5611 | 0.004357 | 3.8219e-05 | 1 | 114 | Unplanned | Unknown cause | Replace Fuses
1246 |  | 3116A-26 | Carroll St | Wairoa | Borough Two 3205 | 2026-03-14 12:00 | 46095.5 | 2026-03-14 14:46 | 46095.6153 | 0.49486 | 0.0029811 | 78 | 6494.9272 | Planned | Planned | To remove faulty ABS W930 and Install new ABS at pole W3137
1247 |  | 1240-26 | Pitchers Road | Gisborne | Te Karaka 1203 | 2026-03-14 12:03 | 46095.5021 | 2026-03-14 12:44 | 46095.5306 | 0.010357 | 0.00026753 | 7 | 271 | Unplanned | Unknown cause | To replace blown HV fuses E315
1248 |  | 6676-26 | 78 Tansley Road | Gisborne | Lavenham 0902 | 2026-03-15 07:18 | 46096.3042 | 2026-03-15 10:40 | 46096.4444 | 0.077202 | 0.00038219 | 10 | 2020 | Unplanned | Unknown cause | Replace Fuses
1249 |  | 3104-26 | Ormond Road | Gisborne | Haisman 0804 | 2026-03-15 08:35 | 46096.3576 | 2026-03-15 16:59 | 46096.7076 | 2.8701 | 0.0056946 | 149 | 35589.0187 | Planned | Planned | To carryout work on 50kV Gis - Makaraka line
1250 |  | 6677-26 | 3 Bond Road | Gisborne | Waimata 0903 | 2026-03-16 06:59 | 46097.291 | 2026-03-16 08:18 | 46097.3458 | 0.060386 | 0.00076438 | 20 | 1580 | Unplanned | Vegetation | Replace Fuses
1251 |  | 3144-26 | Peel Street | Gisborne | Kahutia 0601 | 2026-03-16 07:06 | 46097.2958 | 2026-03-16 07:19 | 46097.3049 | 0.0089432 | 0.00068794 | 18 | 234 | Planned | Planned | Replace TX B936
1252 |  | 3144A-26 | Peel Street | Gisborne | Kahutia 0601 | 2026-03-16 07:19 | 46097.3049 | 2026-03-16 11:50 | 46097.4931 | 0.010357 | 3.8219e-05 | 1 | 271 | Planned | Planned | Replace TX B936
1253 |  | 3136-26 | Tauwhareparae Road | Gisborne | Tauwhareparae 0404 | 2026-03-16 08:39 | 46097.3604 | 2026-03-16 09:23 | 46097.391 | 0.018498 | 0.00042041 | 11 | 484 | Planned | Planned | Carry out Repairs on 11kV pole G1758
1254 |  | 3144B-26 | Peel Street | Gisborne | Kahutia 0601 | 2026-03-16 12:26 | 46097.5181 | 2026-03-16 12:36 | 46097.525 | 0.0068794 | 0.00068794 | 18 | 180 | Planned | Planned | Replace TX B936
1255 |  | 3113-26 | Wharerata Road, Muriwai | Gisborne | Muriwai 0905 | 2026-03-17 09:00 | 46098.375 | 2026-03-17 13:19 | 46098.5549 | 2.5019 | 0.0098987 | 259 | 32892.6242 | Planned | Planned | Replace ABS C129
1256 |  | 3123-26 | Waiapu Rd | Gisborne | Inland 0301 | 2026-03-17 09:08 | 46098.3806 | 2026-03-17 12:57 | 46098.5396 | 0.061074 | 0.00026753 | 7 | 799.1264 | Planned | Planned | Upgrade to recloser @ H55
1257 |  | 1241A-26 | Hereheretau Road | Wairoa | Nuhaka 3203 | 2026-03-17 13:25 | 46098.559 | 2026-03-17 16:21 | 46098.6813 | 0.053812 | 0.00030575 | 8 | 1408 | Unplanned | Defective Equipment | Replace LV poles W8579 & W8580
1258 |  | 3110-26 | Pakowhai Road | Gisborne | Muriwai 0905 | 2026-03-17 19:30 | 46098.8125 | 2026-03-17 22:52 | 46098.9528 | 0.12352 | 0.0006115 | 16 | 960.587 | Planned | Planned | Isolation for house moving
1259 |  | 6678-26 | 14 Ruakaka Road | Gisborne | Tiniroto 1003 | 2026-03-17 20:08 | 46098.8389 | 2026-03-17 22:38 | 46098.9431 | 0.08026 | 0.00053507 | 14 | 2100 | Unplanned | Unknown cause | Replace Fuses
1260 |  | 3122-26 | Mata Road | Gisborne | Mata 0304 | 2026-03-18 09:05 | 46099.3785 | 2026-03-18 14:37 | 46099.609 | 0.2284 | 0.00068794 | 18 | 2990.0556 | Planned | Planned | Replace HV poles
1261 |  | 3117-26 | Wharerata | Gisborne | Muriwai 0905 | 2026-03-18 09:06 | 46099.3792 | 2026-03-18 13:59 | 46099.5826 | 0.078387 | 0.00026753 | 7 | 1025.7744 | Planned | Planned | Remove ABS C189
1262 |  | 6679-26 | 173 Bailie Road | Gisborne | Waimata 0903 | 2026-03-19 08:02 | 46100.3347 | 2026-03-19 09:45 | 46100.4062 | 0.0078731 | 7.6438e-05 | 2 | 206 | Unplanned | Unknown cause | Replace Fuses
1263 |  | 3134-26 | Waimata Road | Gisborne | Tahora 1103 | 2026-03-19 08:35 | 46100.3576 | 2026-03-19 10:45 | 46100.4479 | 0.079496 | 0.0006115 | 16 | 1040.636 | Planned | Planned | To remove faulty ABS D1306 & Jumper through
1264 |  | 3135-26 | Pipiwhakao Road | Gisborne | Lavenham 0902 | 2026-03-19 12:05 | 46100.5035 | 2026-03-19 14:03 | 46100.5854 | 0.081177 | 0.00068794 | 18 | 1062.9287 | Planned | Planned | To Straighten pole D1612, D1611, D708
1265 |  | 6680-26 | 5989 Tiniroto Road | Wairoa | Ruakituri 2003 | 2026-03-19 20:33 | 46100.8562 | 2026-03-20 09:39 | 46101.4021 | 0.06008 | 7.6438e-05 | 2 | 1572 | Unplanned | Unknown cause | Replace Fuses
1266 |  | 3124-26 | Opou Road | Gisborne | Muriwai 0905 | 2026-03-20 08:36 | 46101.3583 | 2026-03-20 09:40 | 46101.4028 | 0.026906 | 0.00042041 | 11 | 352.148 | Planned | Planned | Isolation for tree cutting near 11kV lines
1267 |  | 3125-26 | Mata Road | Gisborne | Mata 0304 | 2026-03-20 09:05 | 46101.3785 | 2026-03-20 16:03 | 46101.6687 | 0.28756 | 0.00068794 | 18 | 3737.5695 | Planned | Planned | To replace 11kV poles H1022, H1021, H1013
1268 |  | 3128-26 | Whangara Road | Gisborne | Dalton 0502 | 2026-03-20 09:13 | 46101.384 | 2026-03-20 13:58 | 46101.5819 | 0.021785 | 7.6438e-05 | 2 | 285.0229 | Planned | Planned | Isolation for Eastland Treecare to cut trees
1269 |  | 1242-26 | Campion - Elgin - Te Hapara | Gisborne | Campion 0802 | 2026-03-20 10:22 | 46101.4319 | 2026-03-20 15:58 | 46101.6653 | 2.1118 | 0.06417 | 1679 | 55255 | Unplanned | Defective Equipment | Switch mechanism failure, Ring main switch C6528
1270 |  | 6681-26 | 5989 Tiniroto Road | Wairoa | Ruakituri 2003 | 2026-03-20 11:44 | 46101.4889 | 2026-03-20 16:00 | 46101.6667 | 0.019568 | 7.6438e-05 | 2 | 512 | Unplanned | Unknown cause | Replace Fuses
1271 |  | 6682-26 | 593 Waihau Road | Gisborne | Rototahi 0403 | 2026-03-21 07:24 | 46102.3083 | 2026-03-21 10:20 | 46102.4306 | 0.094172 | 0.00053507 | 14 | 2464 | Unplanned | Unknown cause | Replace Fuses
1272 |  | 6683-26 | 322 Waingake Road | Gisborne | Te Arai 0906 | 2026-03-21 07:26 | 46102.3097 | 2026-03-21 12:05 | 46102.5035 | 0.010663 | 3.8219e-05 | 1 | 279 | Unplanned | Unknown cause | Replace Fuses
1273 |  | 3112-26 | Tolaga Bay | Gisborne | Town 0402 | 2026-03-22 09:00 | 46103.375 | 2026-03-22 13:59 | 46103.5826 | 2.3541 | 0.0078731 | 206 | 31040.2792 | Planned | Planned | Replace ABS G48 & G50
1274 |  | 1243-26 | Matakoao | Gisborne | Hicks Bay 0102 | 2026-03-22 10:17 | 46103.4285 | 2026-03-22 10:44 | 46103.4472 | 0.056297 | 0.0098987 | 259 | 1473 | Unplanned | Unknown cause | Tripped CB J523 to allow faultman to close HV fuse J616
1275 |  | 1244-26 | Morere Road | Wairoa | Morere 3401 | 2026-03-22 13:28 | 46103.5611 | 2026-03-22 15:46 | 46103.6569 | 0.43669 | 0.0032486 | 85 | 11426 | Unplanned | Defective Equipment | Strain insulator pulled through x-arm - jumper broken
1276 |  | 6684-26 | 846 Kopuapounamu Road | Gisborne | Awatere 0101 | 2026-03-22 15:52 | 46103.6611 | 2026-03-22 17:20 | 46103.7222 | 0.047086 | 0.00053507 | 14 | 1232 | Unplanned | Unknown cause | Replace Fuses
1277 |  | 6685-26 | 757 Whakaangiangi Road | Gisborne | Awatere 0101 | 2026-03-22 18:08 | 46103.7556 | 2026-03-22 20:20 | 46103.8472 | 0.01009 | 7.6438e-05 | 2 | 264 | Unplanned | Unknown cause | Replace Fuses
1278 |  | 1245-26 | Lake Road, Cricklewood Road | Wairoa | Frasertown 3103 | 2026-03-23 10:57 | 46104.4563 | 2026-03-23 12:56 | 46104.5389 | 0.22282 | 0.0019109 | 50 | 5830 | Unplanned | Defective Equipment | To Replace broken 11kV X-arm on pole W4823
1279 |  | 6686-26 | 663 Rangitukia Road | Gisborne | Tiki Tiki 0206 | 2026-03-23 16:09 | 46104.6729 | 2026-03-23 17:45 | 46104.7396 | 0.007338 | 7.6438e-05 | 2 | 192 | Unplanned | Unknown cause | Replace Fuses
1280 |  | 3119F-26 | Ihungia Road | Gisborne | Mata 0304 | 2026-03-24 08:40 | 46105.3611 | 2026-03-24 15:34 | 46105.6486 | 0.047468 | 0.00011466 | 3 | 1242 | Unplanned | Human Error | Isolation to cut trees between pole H4154-H4187. Not advertised within 24hrs notice
1281 |  | 3126-26 | Mata Road | Gisborne | Mata 0304 | 2026-03-24 09:03 | 46105.3771 | 2026-03-24 14:32 | 46105.6056 | 0.22633 | 0.00068794 | 18 | 2963.037 | Planned | Planned | Replace 11kV poles
1282 |  | 3118-26 | Kaiwaitau Road | Wairoa | Mahia 3301 | 2026-03-24 09:06 | 46105.3792 | 2026-03-24 16:12 | 46105.675 | 0.56985 | 0.0013377 | 35 | 7254.6914 | Planned | Planned | Replace HV poles W674
1283 |  | 3142A-26 | Hirini Street | Gisborne | Esplanade 1503 | 2026-03-25 07:05 | 46106.2951 | 2026-03-25 07:29 | 46106.3118 | 0.01009 | 0.00042041 | 11 | 132.0555 | Planned | Planned | Replace Ring Main Unit A391, A390, A392, A393
1284 |  | 6687-26 | 15 Takapau Road | Gisborne | Tauwhareparae 0404 | 2026-03-25 13:00 | 46106.5417 | 2026-03-25 14:42 | 46106.6125 | 0.031187 | 0.00030575 | 8 | 816 | Unplanned | Unknown cause | 8A DDO Fuse
1285 |  | 1246-26 | Te Araroa | Gisborne | Awatere 0101 | 2026-03-25 13:47 | 46106.5743 | 2026-03-25 13:55 | 46106.5799 | 0.027518 | 0.0034397 | 90 | 720 | Unplanned | Unknown cause | Te Araroa Gen4 CB1 tripped causing total blackout to Te Araroa Sub, Te Araroa Sub was running island mode. Refer SE 4716
1286 |  | 1246-26 | Te Araroa | Gisborne | Te Araroa 0103 | 2026-03-25 13:47 | 46106.5743 | 2026-03-25 13:58 | 46106.5819 | 0.052972 | 0.0048156 | 126 | 1386 | Unplanned | Unknown cause | Te Araroa Gen4 CB1 tripped causing total blackout to Te Araroa Sub, Te Araroa Sub was running island mode. Refer SE 4716
1287 |  | 1246-26 | Te Araroa | Gisborne | Hicks Bay 0102 | 2026-03-25 13:47 | 46106.5743 | 2026-03-25 14:05 | 46106.5868 | 0.13239 | 0.0098987 | 259 | 3464 | Unplanned | Unknown cause | Te Araroa Gen4 CB1 tripped causing total blackout to Te Araroa Sub, Te Araroa Sub was running island mode. Refer SE 4716
1288 |  | 6688-26 | 571 Bushmere Road | Gisborne | Waimata 0903 | 2026-03-25 13:50 | 46106.5764 | 2026-03-25 14:37 | 46106.609 | 0.0089815 | 0.00019109 | 5 | 235 | Unplanned | Third Party Interference | Car was gone from site when arrived
1289 |  | 3142B-26 | Hirini Street | Gisborne | Esplanade 1503 | 2026-03-25 17:36 | 46106.7333 | 2026-03-25 17:51 | 46106.7438 | 0.0063061 | 0.00042041 | 11 | 82.5347 | Planned | Planned | Replace Ring Main Unit A391, A390, A392, A393
1290 |  | 3145-26 | Whakaki | Wairoa | Nuhaka 3203 | 2026-03-26 08:30 | 46107.3542 | 2026-03-26 12:48 | 46107.5333 | 1.1695 | 0.0045481 | 119 | 12477.5666 | Planned | Planned | Install Solid Links @ W7888, LFI @ W972, and solid links @ W8166 & W8167
1291 |  | 1248-26 | SH2 Whakaki | Wairoa | Nuhaka 3203 | 2026-03-26 08:33 | 46107.3562 | 2026-03-26 12:48 | 46107.5333 | 0.22415 | 0.00087904 | 23 | 5865 | Unplanned | Human Error | TX were not advertised for SW3145
1292 |  | 1247-26 | SH2 Nuhaka | Wairoa | Morere 3401 | 2026-03-26 08:44 | 46107.3639 | 2026-03-26 10:34 | 46107.4403 | 0.058857 | 0.00053507 | 14 | 1540 | Unplanned | Vegetation | Cleared hazardous tree @ pole W8687
1293 |  | 3127-26 | Mata Road | Gisborne | Mata 0304 | 2026-03-26 09:02 | 46107.3764 | 2026-03-26 13:01 | 46107.5424 | 0.16442 | 0.00068794 | 18 | 2152.8574 | Planned | Planned | Replace HV poles
1294 |  | 3158-26 | Mary Street | Gisborne | Haisman 0804 | 2026-03-26 09:18 | 46107.3875 | 2026-03-26 10:47 | 46107.4493 | 0.29253 | 0.0032868 | 86 | 7654 | Planned | Planned | Install Line fault indicator @ HV links B405
1295 |  | 3146-26 | McLean Street | Wairoa | Brickworks 3201 | 2026-03-26 13:14 | 46107.5514 | 2026-03-26 13:29 | 46107.5618 | 0.037264 | 0.0024842 | 65 | 488.7111 | Planned | Planned | Install LFI @ W3087
1296 |  | 3147-26 | Waihi Road | Wairoa | Frasertown 3103 | 2026-03-26 15:33 | 46107.6479 | 2026-03-26 15:55 | 46107.6632 | 0.010931 | 0.00049685 | 13 | 143.071 | Planned | Planned | Install LFI at Pole W1024
1297 |  | 6689-26 | 248 Waiomoko road | Gisborne | Dalton 0502 | 2026-03-26 16:18 | 46107.6792 | 2026-03-26 17:32 | 46107.7306 | 0.059392 | 0.0008026 | 21 | 1554 | Unplanned | Unknown cause | Replace Fuses
1298 |  | 6690-26 | 220 Ruataniwha Road | Wairoa | Brickworks 3201 | 2026-03-26 21:45 | 46107.9062 | 2026-03-26 22:45 | 46107.9479 | 0.08026 | 0.0013377 | 35 | 2100 | Unplanned | Unknown cause | Replace Fuses
1299 |  | 3164-26 | Kahutia Street | Gisborne | Reads Quay 0603 | 2026-03-27 07:00 | 46108.2917 | 2026-03-27 07:48 | 46108.325 | 0.031187 | 0.00064972 | 17 | 816 | Planned | Planned | Replenish oil RMU B6201 - B6202 - B1099 - B1899 - B1100
1300 |  | 6691-26 | 1737 Ohuka Road | Wairoa | Ruakituri 2003 | 2026-03-27 08:52 | 46108.3694 | 2026-03-27 12:00 | 46108.5 | 0.064667 | 0.00034397 | 9 | 1692 | Unplanned | Unknown cause | Replace Fuses
1301 |  | 3165-26 | Ropata Street | Gisborne | Esplanade 1503 | 2026-03-27 11:04 | 46108.4611 | 2026-03-27 11:31 | 46108.4799 | 0.089776 | 0.0033251 | 87 | 2349 | Planned | Planned | Replenish oil RMU A337 - A339 - A340
1302 |  | 6692-26 | 320 Hereheretau Road | Wairoa | Nuhaka 3203 | 2026-03-27 13:45 | 46108.5729 | 2026-03-27 14:30 | 46108.6042 | 0.030957 | 0.00068794 | 18 | 810 | Unplanned | Unknown cause | Replace Fuses
1303 |  | 1249-26 | Tuakau Road, Ihungia Road | Gisborne | Mata 0304 | 2026-03-27 14:16 | 46108.5944 | 2026-03-27 19:15 | 46108.8021 | 0.14772 | 0.00057328 | 15 | 3865 | Unplanned | Vegetation | Plantation Trees through conductor in two different locations. H1260-H1254 and H638-H639. Wet and windy conditions
1304 |  | 1249-26 | Tuakau Road, Ihungia Road | Gisborne | Inland 0301 | 2026-03-27 15:25 | 46108.6424 | 2026-03-27 15:29 | 46108.6451 | 0.0010701 | 0.00026753 | 7 | 28 | Unplanned | Vegetation | Plantation Trees through conductor in two different locations. H1260-H1254 and H638-H639. Wet and windy conditions
1305 |  | 6693-26 | 213 Brown Beach Road | Gisborne | Muriwai 0905 | 2026-03-27 19:43 | 46108.8215 | 2026-03-27 21:04 | 46108.8778 | 0.02167 | 0.00026753 | 7 | 567 | Unplanned | Unknown cause | Replace Fuses
1306 |  | 3129-26 | Waihua - Raupunga - Mohaka | Wairoa | Raupunga 3101 | 2026-03-28 08:33 | 46109.3562 | 2026-03-28 11:01 | 46109.459 | 1.1426 | 0.0077202 | 202 | 15063.4021 | Planned | Planned | Install LFI's & replace TX W76
1307 |  | 3129A-26 | Waihua - Raupunga - Mohaka | Wairoa | Raupunga 3101 | 2026-03-28 08:33 | 46109.3562 | 2026-03-28 11:10 | 46109.4653 | 0.018001 | 0.00011466 | 3 | 235.5568 | Planned | Planned | Install LFI's & replace TX W76
1308 |  | 6694-26 | 1804 Moanui Road | Gisborne | Matawai 1204 | 2026-03-29 07:50 | 46110.3264 | 2026-03-29 10:00 | 46110.4167 | 0.06459 | 0.00049685 | 13 | 1690 | Unplanned | Unknown cause | Replace Fuses
1309 |  | 1250-26 | Matawai Road | Gisborne | Matawai 1204 | 2026-03-30 09:03 | 46111.3771 | 2026-03-30 11:24 | 46111.475 | 0.25718 | 0.0019492 | 51 | 6729 | Unplanned | Third Party Interference | Truck O/Head HV conductor when dumping shingle - no damage to conductor
1310 |  | 3140-26 | Whakarau Road | Gisborne | Matawai 1204 | 2026-03-31 08:30 | 46112.3542 | 2026-03-31 13:01 | 46112.5424 | 0.18643 | 0.00068794 | 18 | 2441.0432 | Planned | Planned | Replace HV poles
1311 |  | 3132-26 | SH2 Nuhaka, Morere | Wairoa | Morere 3401 | 2026-03-31 09:00 | 46112.375 | 2026-03-31 13:12 | 46112.55 | 0.77049 | 0.0030575 | 80 | 9629.3522 | Planned | Planned | Replace HV pole W8032 & clear trees
1312 |  | 3133-26 | Anaura Road | Gisborne | Mata 0304 | 2026-03-31 09:00 | 46112.375 | 2026-03-31 13:07 | 46112.5465 | 0.53809 | 0.0021785 | 57 | 7058.126 | Planned | Planned | Replace HV pole
1313 |  | 3171-26 | Centennial Drive | Gisborne | Childers 0605 | 2026-03-31 09:02 | 46112.3764 | 2026-03-31 09:49 | 46112.409 | 0.17424 | 0.0037072 | 97 | 4559 | Planned | Planned | Replenish oil in RMU B500
1314 |  | 6695-26 | 5989 Tiniroto Road | Wairoa | Ruakituri 2003 | 2026-03-31 11:58 | 46112.4986 | 2026-03-31 15:15 | 46112.6354 | 0.015058 | 7.6438e-05 | 2 | 394 | Unplanned | Unknown cause | Wind - Replace fuses
1315 |  | ¹ Extend table as necessary to disclose information for all individual interruptions